# Calculating the Diameter of the Pipe:

### Used Formula:

Q=Av

Where,

Q= Peak Demand A= Area of the Pipe

V= Velocity of Water

A= πr2

Where,

r= radius of Pipe

### Assumptions:

Velocity is assumed, V = 3 fps

### Calculations (for Node 21, 22):

Peak demand= 921604 lpd

= (921604×3.28×3.28×3.28)/(1000*3600*24) ft3/s

= 0.380 ft3/s Length of Pipe = 206 ft

Area of pipe = (0.685×144)/3 in2

= 18.261 in2

Diameter of pipe = √ (18.261×4/3.14) in

= 4.823 in

≈ 6 in

| Calculation of Pipe Diameter(Branch Pipe) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Node | Peak Demand (lpd) | Peak Demand (ft3/s) | Length (ft) | Area of Pipe Required (in2) | Diameter of Pipe Required(in) | Diameter of Provided Pipe (in) |
| 27,28 | 27231 | 0.011 | 478 | 0.540 | 0.829 | 2 |
| 24,27 | 30255 | 0.012 | 122 | 0.599 | 0.874 | 2 |
| 26,25 | 816000 | 0.337 | 292 | 16.169 | 4.538 | 6 |
| 25,24 | 819591 | 0.338 | 118 | 16.240 | 4.548 | 6 |
| 24,23 | 849846 | 0.351 | 223 | 16.839 | 4.632 | 6 |
| 22,23 | 880354 | 0.363 | 366 | 17.444 | 4.714 | 6 |
| 21,22 | 921604 | 0.380 | 206 | 18.261 | 4.823 | 6 |
| 15,21 | 1036354 | 0.428 | 99 | 20.535 | 5.115 | 6 |
| 20,19 | 92575 | 0.038 | 160 | 1.834 | 1.529 | 2 |
| 19,18 | 141950 | 0.059 | 103 | 2.813 | 1.893 | 2 |
| 18,17 | 238218.5 | 0.098 | 106 | 4.720 | 2.452 | 4 |
| 17,16 | 281418.5 | 0.116 | 113 | 5.576 | 2.665 | 4 |
| 16,15 | 336138.5 | 0.139 | 185 | 6.660 | 2.913 | 4 |
| 14,13 | 49375 | 0.020 | 168 | 0.978 | 1.116 | 2 |
| 13,12 | 255975 | 0.106 | 210 | 5.072 | 2.542 | 4 |
| 12,11 | 303783 | 0.125 | 121 | 6.019 | 2.769 | 4 |
| 11,10 | 373983 | 0.154 | 178 | 7.410 | 3.072 | 4 |
| 8,7 | 11777.6 | 0.005 | 187 | 0.233 | 0.545 | 2 |
| 7,6 | 23117.6 | 0.010 | 267 | 0.458 | 0.764 | 2 |
| 6,3 | 46517.6 | 0.019 | 206 | 0.922 | 1.084 | 2 |
| 5,4 | 226800 | 0.094 | 258 | 4.494 | 2.393 | 4 |
| 4,3 | 249840 | 0.103 | 97 | 4.950 | 2.511 | 4 |
| 3,2 | 296357.6 | 0.122 | 420 | 5.872 | 2.735 | 4 |
| 2,1 | 446357.6 | 0.184 | 209 | 8.844 | 3.357 | 4 |
| 9,1 | 596357.6 | 0.246 | 74 | 11.816 | 3.880 | 4 |
| 10,9 | 619877.6 | 0.256 | 157 | 12.283 | 3.956 | 4 |
| 15,10 | 993860.6 | 0.410 | 320 | 19.693 | 5.009 | 6 |

# Checking Pressure at the end of Pipe:

### Used Formula:

Head Loss, hf = (4fLv2)/(2gD)

Where

L= length of pipe (ft.) v = velocity (fps)

f= friction factor

D = diameter of the pipe (ft.)

### Assumptions:

Velocity is assumed 3 fps Friction Factor is assumed 0.01 g is assumed 32 ft./s2 Overhead Tank Height = 115 ft

Available pressure at Overhead Tank = (110*62.4)/144 = 50 psi Minimum available pressure at any point must be minimum 30 psi

Sample Calculation (for Path 3):

Node 15, 16:

Length = 185 ft.

Diameter of the provided pipe = 4 in

= 0.333 ft.

Head Loss = (4×0.01×185×3×3)/(2×32×0.333)ft.

= 3.122 ft.

=(3.122×62.4)/144 psi

= 1.353 psi

Node 16, 17:

Length = 113 ft.

Diameter of the provided pipe = 4 in

= 0.333 ft.

Head Loss = (4×0.01×113×3×3)/(2×32×0.333)ft.

= 1.907 ft.

=(3.122×62.4)/144 psi

= 0.826 psi

Node 17, 18:

Length = 106 ft.

Diameter of the provided pipe = 4 in

= 0.333 ft.

Head Loss = (4×0.01×106×3×3)/(2×32×0.333)ft.

= 1.789 ft.

=(1.789×62.4)/144 psi

= 0.775 psi

Node 18, 19:

Length = 103 ft.

Diameter of the provided pipe = 2 in

= 0.167 ft.

Head Loss = (4×0.01×103×3×3)/(2×32×0.167)ft.

= 3.476 ft.

=(3.476×62.4)/144 psi

= 1.506 psi

Node 19, 20:

Length = 160 ft.

Diameter of the provided pipe = 2 in

= 0.167 ft.

Head Loss = (4×0.01×160×3×3)/(2×32×0.167)ft.

= 5.400 ft.

=(3.122×62.4)/144 psi

= 2.340 psi

Total Head Loss = (1.353+0.826+0.775+1.506+2.340) psi

=6.801 psi

Available Pressure = (50 – 6.801) psi = 43.199 psi Which is higher than 30 psi pressure.

So, we do not need to change the diameter of pipe.

| Check of Pipe Diameter(Branch Pipe) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Path | Node | Length (ft) | Diameter of the provided pipe (in) | Diameter of the provided pipe (ft) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Available Pressure | Comment |
| 1 | 15,21 | 99 | 6 | 0.500 | 1.114 | 0.483 |  |  |  |
|  | 21,22 | 206 | 6 | 0.500 | 2.318 | 1.004 |  |  |  |
|  | 22,23 | 366 | 6 | 0.500 | 4.118 | 1.784 |  |  |  |
|  | 23,24 | 223 | 6 | 0.500 | 2.509 | 1.087 | 6.357 | 43.643 | OK |
|  | 24,25 | 118 | 6 | 0.500 | 1.328 | 0.575 |  |  |  |
|  | 25,26 | 292 | 6 | 0.500 | 3.285 | 1.424 |  |  |  |
| 2 | 15,21 | 99 | 6 | 0.500 | 1.114 | 0.483 |  |  |  |
|  | 21,22 | 206 | 6 | 0.500 | 2.318 | 1.004 |  |  |  |
|  | 22,23 | 366 | 6 | 0.500 | 4.118 | 1.784 | 13.133 | 36.867 | OK |
|  | 23,24 | 223 | 6 | 0.500 | 2.509 | 1.087 |  |  |  |
|  | 24,27 | 122 | 2 | 0.167 | 4.118 | 1.784 |  |  |  |
|  | 27,28 | 478 | 2 | 0.167 | 16.133 | 6.991 |  |  |  |
| 3 | 15,16 | 185 | 4 | 0.333 | 3.122 | 1.353 |  |  |  |
|  | 16,17 | 113 | 4 | 0.333 | 1.907 | 0.826 |  |  |  |
|  | 17,18 | 106 | 4 | 0.333 | 1.789 | 0.775 | 6.801 | 43.199 | OK |
|  | 18,19 | 103 | 2 | 0.167 | 3.476 | 1.506 |  |  |  |
|  | 19,20 | 160 | 2 | 0.167 | 5.400 | 2.340 |  |  |  |
| 4 | 15,10 | 320 | 6 | 0.500 | 3.600 | 1.560 |  |  |  |
|  | 10,11 | 178 | 4 | 0.333 | 3.004 | 1.302 |  |  |  |
|  | 11,12 | 121 | 4 | 0.333 | 2.042 | 0.885 | 7.739 | 42.261 | OK |
|  | 12,13 | 210 | 4 | 0.333 | 3.544 | 1.536 |  |  |  |
|  | 13,14 | 168 | 2 | 0.167 | 5.670 | 2.457 |  |  |  |
| 5 | 15,10 | 320 | 6 | 0.500 | 3.600 | 1.560 |  |  |  |
|  | 10,9 | 157 | 4 | 0.333 | 2.649 | 1.148 |  |  |  |
|  | 9,1 | 74 | 4 | 0.333 | 1.249 | 0.541 |  |  |  |
|  | 1,2 | 209 | 4 | 0.333 | 3.527 | 1.528 | 10.445 | 39.555 | OK |
|  | 2,3 | 420 | 4 | 0.333 | 7.088 | 3.071 |  |  |  |
|  | 3,4 | 97 | 4 | 0.333 | 1.637 | 0.709 |  |  |  |
|  | 4,5 | 258 | 4 | 0.333 | 4.354 | 1.887 |  |  |  |
| 6 | 15,10 | 320 | 6 | 0.500 | 3.600 | 1.560 |  |  |  |
|  | 10,9 | 157 | 4 | 0.333 | 2.649 | 1.148 |  |  |  |
|  | 9,1 | 74 | 4 | 0.333 | 1.249 | 0.541 |  |  |  |
|  | 1,2 | 209 | 4 | 0.333 | 3.527 | 1.528 |  |  |  |
|  | 2,3 | 420 | 4 | 0.333 | 7.088 | 3.071 | 17.501 | 32.499 | OK |
|  | 3,6 | 206 | 2 | 0.167 | 6.953 | 3.013 |  |  |  |
|  | 6,7 | 267 | 2 | 0.167 | 9.011 | 3.905 |  |  |  |
|  | 7,8 | 187 | 2 | 0.167 | 6.311 | 2.735 |  |  |  |

Calculating the Flow through different kinds of pipes:

#### Used Formula:

- Hazen-Williams formula:

#### H= kQx (m)

Where,

H = head Loss

K = is a constant depending on length, diameter and roughness of the pipe as well as fluid property.

Here, we are assuming k=1

Q = Assumed flow in the pipe (m3/s) X = 1.85 for Hazen Williams equation

- Calculation of correction Δ :

#### Δ = - ΣH / (x ΣH/Q )

Where,

Δ = Correction to be applied in each loop Q = Flow through the pipe

Assumptions:

Algebraic sum of head loss in a closed loop will be zero.

∑ Inflow = ∑Outflow Water Calculations : Total Water Demand :

#### For AEFGA Loop:

Total Water =( Sewing+Printing+Cutting+Finishing+ Vehicle Parking+Storing+0.5*Production)

= (12600+12600+12600+6667.2+682.5+7087.5+0.5*756000)

= 417637.2 lpd

= 0.0128 m3/s

#### For AEDCBA Loop:

Total Water = (Raw Material+Washing+Weaving+Storing+ WasteDumping+Knitting+Spinning+Dying+ Finishing+ETP+0.5*Production)

= (3307.5+12600+10605+6825+682.5+10605+12600+ 11550+7875+1680+0.5*756000)

= 456330 lpd

= 0.0168m3/s

#### Calculations for Loop Method (for Node 21, 22):

909’ A

678’ A

928’ A

766’

## For Loop AEFGA:

For Pipe AE:

Length = 277 m

Assumed Discharge, Q0 = 0.01 m3/s Headloss, H0 = kQ01.85 = 1*0.011.85=0.000200 m Now, H0/Q0 = 0.000200/0.01 =0.0200

From The Chart below We get,

∆ = 1.2E-03

## For Loop AEDCBA:

For Pipe AE following similar Process as above we get,

∆ = -2.4E-05

1587’

So Total Corrected Flow for Pipe AE = 0.01+0.0012- 0.000024 = 0.0123 m3/s

## Initial Assumption

.0128

F

G

.0032

.0096

.0068

.01

D

E

A

.01

C

B

.0068

.0096

.0296

.0068

## Table for the 1st trial:

.0168

| Loop | Notation | Length (m) | Qo (m3/s) | Ho (m) | Ho/Qo |  (m3/s) | Qf (m3/s) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABCDEA | AB | 234 | 0.0100 | 0.000200 | 0.0200 | -0.000024 | 0.01 |
|  | BC | 484 | 0.0100 | 0.000200 | 0.0200 | -0.000024 | 0.01 |
|  | CD | 234 | -0.0068 | -0.000098 | 0.0144 | -0.000024 | -0.0068 |
|  | DE | 207 | -0.0068 | -0.000098 | 0.0144 | -0.000024 | -0.0068 |
|  | EA | 277 | -0.0100 | -0.000200 | 0.0200 | -0.000024 | -0.012 |
|  |  |  |  |  |  | 0.0012 |  |
|  |  |  |  | 0.000004 | 0.0886095 |  |  |

- ΣHo / (x

	ΣHo/Qa)

=	-0.000024

| Loop | Notation | Length (m) | Qo (m3/s) | Ho (m) | Ho/Qo |  (m3/s) | Qf (m3/s) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| AEFGA | AE | 277 | 0.01000 | 0.00020 | 0.0200 | 0.0012 | 0.012 |
|  |  |  |  |  |  | -0.000024 |  |
|  | EF | 283 | 0.00320 | 0.00002 | 0.0076 | 0.0012 | 0.0044 |
|  | FG | 277 | -0.00960 | -0.00019 | 0.0193 | 0.0012 | -0.0084 |
|  | GA | 283 | -0.00960 | -0.00019 | 0.0193 | 0.0012 | -0.0084 |
|  |  |  |  | -0.00015 | 0.066 |  |  |

	- ΣHo / (x ΣHo/Qa)

=	0.0012

## Flow after 1st trial:

.0128

F

.0084

G

.0044

.0084

.0068	.01

D	E	A

.0296

.0068

.01

C	B

.01

## Table for the 2nd trial:

.0168

| Loop | Notation | Length (m) | Qo (m3/s) | Ho (m) | Ho/Qo |  (m3/s) | Qf (m3/s) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABCDEA | AB | 234 | 0.01 | 0.0001986 | 0.0199 | 0.0000000064 | 0.01 |
|  | BC | 484 | 0.01 | 0.0001986 | 0.0199 | 0.0000000064 | 0.01 |
|  | CD | 234 | -0.0068 | -0.0000984 | 0.0144 | 0.0000000064 | -0.0068 |
|  | DE | 207 | -0.0068 | -0.0000984 | 0.0144 | 0.0000000064 | -0.0068 |
|  | EA | 277 | -0.012 | -0.0002004 | 0.0200 | 0.0000000064 | -0.011 |
|  |  |  |  |  |  | -0.0000025 |  |

	- ΣHo / (x ΣHo/Qa)

=	0.0000000064

-1.05252E-09	0.0886559

| Loop | Notation | Length (m) | Qo (m3/s) | Ho (m) | Ho/Qo |  (m3/s) | Qf |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | (m3/s) |
| AEFGA | AE | 277 | 0.01120 | 0.0002459 | 0.0220 | -0.0000025 | 0.011 |
|  |  |  |  |  |  | 0.0000000064 |  |
|  | EF | 283 | 0.00440 | 0.0000436 | 0.0099 | -0.0000025 | 0.0044 |
|  | FG | 277 | -0.00840 | -0.0001446 | 0.0172 | -0.0000025 | -0.0084 |
|  | GA | 283 | -0.00840 | -0.0001446 | 0.0172 | -0.0000025 | -0.0084 |

0.0000003036	0.0663082

	- ΣHo / (x ΣHo/Qa)

=	-0.0000025

## Flow after 2nd Trial:

.0128

F

G

.0044

.0084

.0068

.01

D

E

A

.01

C

B

.01

.0044

.0296

.0068

.0168

## Calculating the Diameter of different Pipes:

#### Provided values:

For C = 120

| Pipe | Qf (m3/s) | Qf ft^3/s | length (ft) | H0 Per 1000' for C=100 (ft) | H0 for C=100 ft | H0 for C=120 | Q (l/s) | Headloss per unit length (m/m) | Dia provided (mm) | Dia provided (inch) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AB | 0.0100 | 0.3522 | 768 | 25 | 19.188 | 16 | 9.98 | 0.021 | 100 | 4 |
| BC | 0.0100 | 0.3522 | 1588 | 25 | 39.688 | 33 | 9.98 | 0.021 | 100 | 4 |
| CD | 0.0068 | 0.2410 | 768 | 30 | 23.0256 | 19 | 6.82 | 0.025 | 85 | 4 |
| AE | 0.0112 | 0.3953 | 909 | 20 | 18.18 | 15 | 11.19 | 0.017 | 120 | 5 |
| DE | 0.0068 | 0.2410 | 678 | 30 | 20.34 | 17 | 6.82 | 0.025 | 85 | 4 |
| EF | 0.0044 | 0.1552 | 928 | 40 | 37.12 | 31 | 4.39 | 0.033 | 70 | 3 |
| FG | 0.0084 | 0.2968 | 909 | 26 | 23.634 | 20 | 8.41 | 0.022 | 100 | 4 |
| GD | 0.0084 | 0.2968 | 928 | 26 | 24.128 | 20 | 8.41 | 0.022 | 100 | 4 |

## Diameter of Different Pipes:

G

3”

4”

4”

5”

D

E

A

4

C

B

4”

4”

”

4”