# Drainage System Design

Assumptions:

- Soil stack conveys discharge of water closet.

- Waste stack conveys   discharge of   shower, Sink , Wash basin , ablution Tap etc.

- Vent stack is continued over 2m from roof.

- The whole building is divided into 2 part each having 9 units.

- One soil stack, one waste stack and one vent stack is provided for 9 apartments.

|  |  |  | Design of Waste Stack & Soil Stack |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design of |  |  | Type of Fixture per apartment |  | Number |  | FU value as load factor |  | Total FU from each type of fixture |  | Total FU from an apartment |  | Total FU of one side of a building |  | Required diameter of waste stack |  | Slope of the stack |  |
| Waste Stack |  |  | wash basin |  | 3 |  | 1 |  | 3 |  | 12 |  | 108 |  | 100 mm |  | 0.01 |  |
|  |  |  | ablution tap |  | 1 |  | 1 |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  | shower |  | 3 |  | 2 |  | 6 |  |  |  |  |  |  |  |  |  |
|  |  |  | kitchen sink |  | 1 |  | 2 |  | 2 |  |  |  |  |  |  |  |  |  |
| Soil Stack |  |  | water closet |  | 3 |  | 3 |  | 9 |  | 9 |  | 81 |  | 100 mm |  | 0.01 |  |

Waste Stack Design:

DFU calculation of Each apartment,

- wash basin=3

- ablution tap=1

- shower	=3

- kitchen sink=1

The load factor of different unit is (table 8.6.14)

- wash basin-1

- ablution tap-1

- shower-2

- kitchen sink-2

So, total DFU for an apartment is =3*1+1*1+

3*2+1*2=12

So, total DFU of 9 apartments =12*9=108

From, table 8.6.16- diameter of waste stack is 100 mm

From, table 8.6.17- slope of waste stack is 0.01

Waste Stack Design:

Branch stack :

For Any Storey:

Branch of waste stack in East and West face :

- wash basin=2

- shower	=2

The load factor of different unit is (table 8.6.14)

- wash basin-1

- shower-2

So, total DFU for an apartment is =2*1+2*2=6

From, table 8.6.16- diameter of waste stack is 50mm

Branch of waste stack in North and South face :

- wash basin=1

- ablution tap=1

- shower	=1

- kitchen sink=1

The load factor of different unit is (table 8.6.14)

- wash basin-1

- ablution tap-1

- shower-2

- kitchen sink-2

So, total DFU for an apartment is =1*1+1*1+1*2+1*2=6

So, Diameter of waste stack is 50mm.( from table 8.6.16)

Soil Stack Design:

DFU of each apartment ;

- Water closet=3

- Load factor of water closet =3

So, total DFU for an apartment is=3*3=9

So, total DFU of 9 apartments =9*9=81

So, Diameter of soil stack is 100 mm (from  table 8.6.16)

So, Slope of soil stack is 0.01 (from table 8.6.17)

Design of vent stack:

Total FU including both soil & waste stack=189 (9 apartments)

Diameter of soil/waste stack 100 mm

Maximum Developed length of vent stack=90+10=100’=30.48m

From table 8.6.21-Diameter of Vent Stack=75 mm

|  | Design of Vent Pipe |  |  |  |
| --- | --- | --- | --- | --- |
| Total FU including both soil & waste stack (DFU) | diameter of soil/waste stack (mm) | Maximum Developed length of vent stack |  | Diameter of Vent Stack (mm) |
|  |  | Ft | m |  |
| 189 | 100 | 100 | 30.48 | 75 |