Chapter 1

Objective:

The objective of this assignment is to design an organogram, and preliminary layout of an Industrial

Village.

Introduction:

An organizational chart / organogram is a diagram that shows the structure of an organization and the

relationships and relative ranks / hierarchy of its parts and positions.

Typical Controlling Wings in an Industry:

Industrial Production Wing

Administrative Wing

Commercial Wing

Human Resource Management Wing

Social Welfare & Management Wing

LAYOUT / PLAN OF THE INDUSTRIAL VILLAGE

• Making the plan or layout is one of the preliminary task for overall design of the industrial village.

• An ideal layout of individual zones/ units of the industrial village is an important factor for smooth & efficient

functionality of the industrial processes.

Layout should include the following:

▪ Layout should be drawn in AutoCAD in appropriate scale.

▪ Proper layering should be incorporated in the drawing so that different parts like: overall layout, water

Distribution network, sewer network can be separately visible if needed.

▪ The layout should show the north direction and the assumed scale.

▪ Administrative Zone, Industrial Zone (Including individual units),Residential Zone, Common Service

Area, etc. should be shown clearly in layout.

▪ Assume a highway is on one side of the village and a river flowing along opposite side.

▪ Internal road network should be clearly visible in the layout.

▪The road network should be designed considering route for incoming raw material and outgoing finished products.

▪The ETP location The ETP location should be such that the treated effluent can be discharged in the adjacent river.

▪ In the residential zone separate types of quarters should be allocated for employees of

different administrative status (e.g. bungalow for the Chairman, six –storied aparment buildings for 1st class

employees, dorm for 2nd 3rd & 4th class employees etc.)

▪Common facilities like School, Mosque, Hospital, Community center, Bank, ATM, Super store, Parking,

Canteen etc. should be included.

▪ Provisions of parks, playing fields, green spaces, gardens should be provided in the village.

▪ Provisions for future land area expansion for different types of zones (e.g. residential, industrial)

should be kept while preparing the layout.

▪Common facilities like School, Mosque, Hospital, Community center, Bank, ATM, Super store,

Parking, Canteen etc. should be included.

▪ Provisions of parks, playing fields, green spaces, gardens should be provided in the village.

▪ Provisions for future land area expansion for different types of zones (e.g. residential, industrial)

should be kept while preparing the layout.

Organogram of the Industry

| Total Manpower | 1st class | 2nd class | 3rd class | 4th class |
| --- | --- | --- | --- | --- |
| 1643 | 56 | 118 | 265 | 1204 |

Chapter 2

Objective:

The objective of this assignment is to calculate water demand for different components of the industrial village – present demand, demand after 10 and 20 years.

Introduction:

In an industrial village water is very important. As an Industrial village designed to be operational for at least 30 years so water should also be calculated accordingly. Depending on types of occupation different types of population increase is assumed and water demand is calculated.

Population Estimation:

Population calculation should be made for each zones, i.e.

- Residential,

- Administrative,

- Industrial Production &

- Common Services.

Future population calculation (after 10 years and 20 years) were made with a set of assumptions

on increase of population in different zones of the village.

Residential Population:

• For the residential zone proper considerations were made in calculating family size and accommodation size of different staff members.

• Calculate present population in the residential zone based on organogram for different occupancy types and specific family size.

• Assumed family residence for 1st class and 2nd class employees. For 3rd & 4th class employees provided with dormitory.

• Prediction of future population for a certain design period

Future population = P x (1 + r)n

Here,

P= Present population

r = Growth rate (%)

n = Design period (yrs)

Average family size & annual population growth rate in Bangladesh in 2016 are 4.06 persons/family & 1.1% respectively.

Rather than using exactly these values, we used different growth rate and family size depending on social classification. e.g., for 1st residents, assumed family member = 6 & growth rate – 0.8%

Table showing different occupancy types, family members for each type of occupancy, present residential population, population after 10 years and after 20 years -for each type of occupancy are attached

Population Estimation for Industrial Production:

For the administrative, industrial, and common service zones proper considerations were made for calculating the number of staffs working.

The Organogram was the base line in determining the total population of the industrial village

The assumptions (% of worker/staff staying inside or outside the village) were clearly stated for each calculation.

Assumed feasible future expansion of the industrial production and estimate future population in industrial production after 10 years and 20 years. Table showing each position as in the organogram, number of person(s) occupying that position at present, after 10 years and 20 years is prepared. In similar way estimation of population of administrative and different commercial/ common facilities at present, after 10 years and 20 years. However, for administrative & common facilities, growth rate were lower than the population estimated for industrial production. Table showing estimated population for administrative & common facilities as done for industrial production is attached. A summery table showing total population in different zones – residential, industrial etc. – at present, after 10 years and 20 years is shown.

Water Consumption / Demand Calculation:

• Water demand/requirement can be classified as:

1. Residential water demand.

2. Industrial water demand.

3. Administrative water demand.

4. Water demand for common services.

5. Water demand for fire fighting

• Water requirement for common service should be calculated on basis of operating hours,

occupancy type, and number of people working in each types of service area. Appropriate

assumptions should be mentioned before each calculation.

1. Water requirement for Residential Zone:

Depending on occupancy type, select per capita water consumption (lpcd) as per the BNBC 2006

[Table 8.5.1(a) to (d)]

Calculated water demand in lpd for present population and for the expected design period:

Water consumption (liter/day) = water requirement (lpcd) x water consuming

population.

Fluctuations in Rate of Demand:

Average daily per capita demand can be calculated from-

(Population by total Months 12 in required Water)/( Population 365 )

But if this average demand is supplied at all the times, it will not be sufficient to meet the

fluctuations.

Peak factors:

• Total water consumption/demand were calculated considering suitable peak factors and

time factors to meet instantaneous hourly peak demand.

• These factors for different zones may vary considering occupancy types, operations,

operating hours etc.

Example of peak factors for different zones:

Residential zone = 2.5

Industrial zone = 1.4

Administrative zone = 1.4

Common Facility zone = 4

Firefighting = 1

Time Factor:

For other zones except residential area, water supply requirement is less than 24 hours. e.g., for

office and most of the commercial facilities water supply is required only during working hours,

commonly 8-hrs.

That means the water demand calculated using average consumption rate is being consumed within

this 8 hours. Therefore, the demand water for any facility must be supplied within this consumption

period not over 24 hours. So some time factor must be applied in calculating water demand.

Time factor (TF) for industrial area (assuming two shifts- each shift of 8-hrs)

= 24/ (8x2) = 1.5 (for production demand)

TF for residential area = 24/24 = 1, TF for school = 24/6 = 4 etc.

Water demand for any facility/zone = avg. water demand (lpd) x PF x TF

2. Water requirement for industrial zone

Water requirement for industrial purpose should include two aspects:

(a) water use for industrial production,

(b) water use for personal consumption.

3. Water requirement for common services

Common services include- school, college, hospital, market, parking zone, park, hotel, office, bus

stand, rail station, mosque, community center, auditorium, restaurants, fire service, police station

etc.

Assume different PF & TF for individual type of facilities.

Prepare a similar water demand table for different common services.

4. Water requirement for fire fighting

An adequate amount of water is essential to confining, controlling, and extinguishing hostile fires

in structures. The actual amount of water needed differs based on different building and occupant

conditions.

For our water supply system firefighting water demand is to be calculated for –

- Individual occupancy type (industrial building, commercial building, residential building

etc.): use BNBC 2006 (see table -6)

- Street fire hydrant: Fire hydrant is an outlet used for tapping water during fires. Fire hydrants should be placed-

i) At all street intersections and turnings.

ii) At 80 to 120 m intervals on straight run.

Assumptions for Calculating Fire Hydrant Water Demand:

Only one fire incidence occurs per day

Each point must be served by at least two fire hydrants at a time

Nozzle diameter of the hydrant is 3 inches (2r)

Velocity of water in the pipe is 3 fps (v)

Each hydrant will supply water for 30 minutes (t)

Fire Hydrant Water Demand:

We know, Q = A x v

Where,

A = Area of the pipe, ᴫr2 (ft2)

v = Velocity of water (fps)

Q = Discharge of each hydrant (cfs)

Volume of water for each hydrant VF = Q x t (ft3)

No of hydrant working at a time = 2

Total water volume available per occurrence per day = 2VF

Calculate total water demand per day for firefighting (present + future)

In layout plan show the location of fire hydrants.

Prepare a summary table for present and future water demand considering all types of water requirement. Appropriate assumptions should be mentioned before each calculation. Include all assumptions with sample calculation in the main report with details remaining calculations in the appendix.

Population Estimation

There are three zones

1. Residential Zone

2. Industrial Zone

3. Commercial Zone

Residential Zone

Assumption:

- Average family members for 1st class officer 6 person/family

- Average family members for 2nd   class officer 4 person/family

- Family residence for 1st class and 2nd class employees. For 3rd & 4th class employees we will provide dormitory.

- Growth rate………

Table 2-1: Calculation of Population of Residential Zone

Industrial Zone

Assumption

- Population growth after 10 years= 15%

2.   Population growth after 20 years= 25%

Table 2-2: Calculation of Population of Industrial Zone

Commercial Zone

Assumption

- Population growth after 10 years= 10%

- Population growth after 20 years = 20%

Table 2-3: Calculation of Population of Industrial Zone

Summary of Population Prediction

Chapter 3

Objective:

The objective of the assignment is to develop water source for industrial village – estimation of yield of production, gravel pack design, and determination of number of tube well need for present and future 10 and 20 years.

Introduction:

To supply water location of tube well is an important factor. The most important thing is to supply pure and sufficient water in adequate pressure. To bore a hole it is necessary that the water is free from any kind of dust and particle. Besides the boring should be deep enough to supply enough water in all seasons for next 20 years.

Possible available sources of water:

Surface water

Groundwater

Rainwater Harvesting

Main Considerations for the Selection of a Water Supply Source:

The main considerations for the selection of a source of water supply are:

1. Quantity of Water-

Water available at all times through the year

Should meet all the requirements of the community

2. Quality of Water –

Water at the source should be such that the requirement for treatment is minimum.

3. Cost of the system–

Cost involved in development, operation and maintenance of the water supply system should be reasonably affordable to the consumers.

Water Quality Investigation:

Selection water quality parameters to be investigated depend on the quality requirement for the intendant uses. Water quality analysis includes-

o Collection of water samples and detail analysis/investigation

o Collection of past water quality data from different organizations (DPHE, BWDB etc.)

o Selection of treatment methods to obtain desired water quality.

Water Quality Parameters:

pH, Turbidity, Color, TDS, Fe, Mn, As, CO2, Alkalinity. NO3, F2, Cl2, Fecal Coliform

Water Quality Standards:

Bangladesh EQS, 1997. WHO Guide Line Values

PRODUCTION WELL DEVELOPMENT:

Designing a well for production of water involves selection of proper dimensional factors for the well structures and selection of appropriate materials to be used in its construction. Good design should assure an optimum combination of - performance, long service life and reasonable cost.

The main components of a production well design

1. Selection of soil layers for analysis by examining soil samples obtained from test boring

2. Analysis of soil layers through grain size distribution for selected soil layers

3. Locating the aquifer position and water bearing strata

4. Determination of strainer position and suitable length

5. Design of gravel pack materials

6. Selection of strainer material & size

7. Estimation of yield of well

8. Calculation of number of tube wells required to meet the water demand – at present and

at end of design period

Well Depth:

The expected depth of a well is usually determined from the log of a test drilling or from logs of other nearby wells in the same aquifer, or during the drilling of the production well. Generally, a well is completed to the bottom of the aquifer. Before the main production well drilling, usually 1.5 to 2 inch diameter test drilling is conducted and on the basis of sieve analysis results of soil samples collected from every 10 -ft interval a bore log is prepared.

Well Casing /Housing Pipe Diameter:

The well casing must be larger enough to accommodate the pump and should assure good hydraulic efficiency. The diameter of the well casing should be around two sizes larger than the nominal diameter of the pump. For an anticipated yield of 600 to 1300 gpm, well casing outer diameter ranges from 14 to 16 inch are usually taken.

Well Casing /Housing Pipe Material:

Usually seamless MS pipe is used for bigger diameter (12" to 18") casing pipe. For small diameter (4" to 6") production well uPVC material is also used.

Well Casing /Housing Pipe Length:

Length of casing pipe must be sufficient enough so that well pump remain submerged all the time sufficiently below the maximum pumping water level even after a reasonable operation/ design period (10-20 years) of the tubewell (see figure-2).

Well Screen or Strainer:

Well screen is the part of well pipe which contains slit openings for extraction of water from water bearing strata. A properly constructed well screen should -

 allow water to enter the well freely at low velocity,

 prevent sand from entering with the water, and

 serve as the structural retainer to support the loose formation material.

So the length and position of the strainer must be evaluated carefully. Following four factors to be considered while determining the position of the well screen-

1. Existing static water level at present

2. Assumed drawdown of 10-20 ft while pumping

3. Average rate of water level declination per year x design period

4. Extra allowance of 10-15 ft depth for safety

That means the position the screen should start after providing blank casing up to the extent equal to the sum of the above four values.

Grain Size Distribution Analysis:

The bore log previously prepared using test drill data is used for selection of strainer position. By visual inspection of the collected soil samples of various depths (usually at 10 ft intervals) possible location of strainer is assumed and grain size distribution curve (% Finer vs opening size) for each layer is prepared. From the grain size analysis results the following soil characteristics are determined:

A. Fineness Modulus –

B. Effective Size (D10) –

Size that represents 10 % finer and 90% coarser of soil sample

C. Co-efficient of Uniformity (Cu) = D60/D10

Higher value of Cu > 2.0 indicates well graded sample

D. Percentage distribution of soil particles according to MIT soil classification (Coarse,

Medium, Fine)

Locating the aquifer and water bearing strata:

All soil sample data are summarized in a table to find available water bearing soil strata

Factors to be considered for locating water bearing strata

1.Greater uniformity coefficient increases permeability

2.Higher fineness modulus means bigger soil particle

3.Higher percentage of course and medium sand indicates higher water carrying capacity

FM<1 → Clay and silt

FM=1 → Fine sand with silt

FM>1→ Medium to course sand which has potential to good permeability and presence

of water

Well Screen (Strainer) Length:

The optimum length of well screen is chosen in relation to the thickness of the aquifer available drawdown and stratification of the aquifer.

As it is very difficult to maintain vertical alignment of a long strainer, it will not be practical to go beyond 100' screening. Strainer should not be extended up to the bottom of the aquifer to allow upward converging flow of water during pumping.

Where Blank Pipe is Necessary:

Between two strainers of a discontinuous aquifer

10' blank pipe is placed at the bottom to trap soil particles that may enter the pipe through

upward converging flow

Summary of Grain Size Distribution Curve:

Well Casing Pipe Length:

Existing water table=280’

Water level declination=2’/year

Design period = 20 years

Total declination of water level = 20*2' = 40'

Let drawdown=15’

F.S. =15’

So, length of casing pipe = (280+40+15+15) =350’

Since bore log ends at 460’

We take length of casing pipe=460’

Strainer Location and Length:

Minimum depth of strainer=280+40+15+15=350’

So Strainer may be provided between 360’–450’

Depth of Acquifer=180’

Available Depth= 460 - 350=110’>50’

Length of Strainer=.8x110=88’

We take Strainer length of 90’ (360’-450’)

Selection of Strainer slot no:

Slot Number = Slot size (in mm) x 1000 / 25.4

D10 of Gravel Pack=.85mm

Slot number=.85*1000/25.4=33.5

Let us take Slot size 30

Strainer dia 6’’

Gravel Pack Design:

From depth 360’-450’

F.M. lowest  =1.52

Multiplication factor= 5

D30 at Depth 400-420ft =.24 mm

D30 of gravel pack =.24*5=1.2 mm

Cu of gravel pack=2.11<2.5 (O.K.)

4 inch diameter envelop of gravel pack material will surround the

entire screen.

Yield Calculation

Yield of one well = Area*velocity*Screen blockage factor

Let

Velocity is 0.1 fps

Screen blockage 0.4

Diameter 0.5’

16hrs. Pumping hour

Yield=(π*.5*90*.15*.1*.4) =.848 ft3/sec= (.848*.30483*1000*3600) lph=86469.12 lph

As pumping is done for 18hrs a day, total yield per day = 86469.12×18 lpd

=  1556444.16lpd

Table: Water Demand Summery

Number of tube wells:

Residential area + Commercial area:

Industrial Zone:

Chapter 4

Objective:

The objective of this report is to calculate pump capacity and prepare a pumping schedule of an industrial village.

Introduction:

In order to meet the water demand of our industrial village, we need to find pump capacity. In this report pump capacity is calculated in Horse-power (HP) unit. Also pump schedule is designed, accordingly pumps will be installed and operated for a period of 20 years.

Used Formula:

1. Working Horse Power, WHP = HQ/3960

H = Total head of the pump (ft.)

Q = Yield of well (gpm)

2. Breaking Horse Power, BHP = WHP/ ƞ

ƞ = Pump Efficiency

3. Total Head, H = Static head + Velocity head + Friction head

4. Static head = Suction head + Delivery head

5. Total Delivery Head = Static Water Level + Maximum Building Height

6. Velocity head = v2/2g

7. Maximum Pipe Length = Maximum horizontal distance + Maximum height of building + Height of overhead tank

Assumptions:

1. ƞ is assumed to be 75%.

2. We will use submersible pump, So suction head = 0

3. Friction loss is assumed to be 10% of total pipe length.

4. Height of floor is 10 ft.

5. Velocity is assumed 3 fps.

6. Height of overhead tank is assumed 12’

Sample Calculation:

For Pump 1

Pump capacity:

Static Head = Suction Head (hs) + Delivery Head (hd)

Here Suction head = 0 (Submersible Pump)

Delivery head,

hd  = Static water level + Maximum building height

= 280’+60’ +12’= 352’

Velocity head,

hv= v2/ 2g = 32/(2*32) =0.14’

Friction head,

Maximum pipe length = Maximum horizontal distance + Maximum height of the building

+ Height of overhead tank

= 496’+60’+12’ = 568’

Friction Head = Maximum pipe length* 10%

= 568*0.1 = 56.8’

So, Total head,

H = static head+ velocity head+ friction head

= 352’+.14’+56.8’

= 408.94’

Yield of well,

Q = 64851.84 lph

= 64851.84 /227.13

= 285.53 gpm

WHP = HQ/3960

= (408.94*285.53)/3960

= 29.49 HP

Let, Pump Efficiency  = 75%

BHP = WHP/.75

= 28.65 /0.75

=39.32

Table 4-1:Calculation for Pump Capacity

Table 4-2: Pump Scheduling for Residential & Commercial Zone(Present):

Table 4-3: Pump Scheduling for Residential & Commercial Zone(10 years):

Table 4-4: Pump Scheduling for Residential & Commercial Zone(20 years):

Table 4-5: Pump Scheduling for Industrial Zone(Present):

Table 4-5: Pump Scheduling for Industrial Zone (10 years):

Table 4-5: Pump Scheduling for Industrial Zone (20 years) :

Reference Tables & Figures:

Fig 4-1: Head-Capacity Curve

Chapter 6

Objective:

The objective of this of report is to design sanitary sewer system for the industrial village. In this report we will design trunk sewer for the village.

Introduction:

The basic functional elements of a conventional sewerage system include -

1. House connections- collect wastewater from houses,

2. Network of sewer systems- for collection and conveying the wastewater and

3. Treatment plant- for processing the wastewater, and

4. Receiving environment (water or land) for disposal of the treated wastewater

Depending on the type of sewage carried by the conveyance system, sewage collection can be

categorized into three types-

1. Separate sewerage system

2. Combined sewerage system

3. Partially combined or partially separate system

3 types of sanitary wastewater collection systems based on hydraulic characteristics and purpose:

1. Gravity

2. Pressure

3. Vacuum

In this class we will design Gravity System for Trunk Sewer.

STEPS FOR DESIGN OF TRUNK SEWER

(Sanitary Wastewater only)

1. From the plan of the Industrial Village prepare the layout of wastewater sewer network.

Identify and mark all the junctions (nodes) of branch sewers/main sewers with the Trunk sewer.

2. Calculation of each sub area or service area (in hectors) contributing to each junction/node for determining infiltration rate allowance for each sub area.

3. Calculation of population/unit used under each sub area.

4. Calculation of total average daily water consumption (lpd) for each sub area.

5. Calculation of average wastewater flow per day for each type of unit.

Average ww flow (per day) = multiplying factor (from table-1) x water consumption rate of

the unit per day .

6. Calculation of peak ww flow per day for each unit.

Peak ww flow per day = avg. ww flow per day x peaking factor (PF- from table-2 or figure-2

for residential ww flow).

7. Calculation of infiltration allowance (m3/ha-d) for each sub area using calculated size of

the sub area (Using figure).

Infiltration and in flow (I/I) = infiltration allowance (m3/ha-d) x area (ha).

8. Calculation of Cumulative Peak flow contributing to each node.

Total Flow, Q (m3/sec) = total peak ww flow towards each node + Infiltration and inflow.

9. Determining size of the pipe segment in between two successive nodes using manning formula.

Assume,

- Pipes are flowing full

- Slope of pipe = 0.0033 in/in (minimum slope for smallest available size – table -3)

- n = 0.013 (for new concrete/ pvc pipe)

Using Manning’s equation,

D= 1.548*(𝑛𝑄/√s)0.375

Use next larger size as pipe diameter (Dactual) if the calculated diameter doesn’t match with standard available pipe sizes.

10. Calculation of “Qfull” using Dactual

11. Calculation of velocity, Vfull, using Manning’s equation

Vfull = (1/𝑛)∗(𝐷/4)(2/3)∗𝑠(1/2)

- Checking with V - minimum (self-cleansing velocity) and V –maximum (non-scouring velocity). Revising diameter/ slope to satisfy this factors.

12. Calculation of Q/ Qfull Using Hydraulic element Diagram

Now finding of – d/D and v/Vfull

13. Determine actual V. Check with V - minimum (self-cleansing velocity) and V –maximum (non-scouring velocity). Revise if needed.

14. Preparing sewer design computation tables as shown in class.

15. Preparing longitudinal Profile of the Trunk sewer

Calculation of Wastewater entering each line:

Assumptions:

1. Percentage of average water demand taken from Table 1

2. Peak factors for different facilities taken from Table 2

3. Peak factors for Residential zone taken from Figure 2

Sample Calculation (for line 1):

For Contributing Area A1

Area description: Shopping Mall, Bazar, Convention Hall, First Class and Second Class Quarter, Chairman Bungalow, Mosque, Day Care Center, Swimming Pool, School & College, Playground, Water Pumping Station.

Average Demand:Residential=413280 lpd,Commercial= 101376lpd, Industrial 0 lpd,

Institutional 231984lpd

Average Wastewater:

Average Wastewater= (0.75*413280+0.75*101376+0.9*0+0.70*231984) lpd

= 548381 lpd

Peak Wastewater:

Peak Wastewater = (3.34*0.75*413280 + 1.8*0.75*101376

+2.1*0.9*0+4*0.75*231984) lpd

= 1821679 lpd

Calculating the amount of Wastewater:

Assumptions:

- Average infiltration rate is taken from Figure 1

Sample Calculation (for line 1):

For Contributing Area A1

Total Area = 7.7 ha.  Average Infiltration Rate = 8.75 m3/ha.d

Infiltration and Inflow = 7.7 *8.75*1000lpd = 67375 lpd

Calculating the Diameter of the Pipe:

Used Formula:

- Manning’s Equation

D= 1.548*(𝑛𝑄/√s)0.375

Here,

D = Diameter of the Pipe

s = Slope of the Pipe

Q = Cumulative flow

Assumptions:

1. s is assumed 0.005 mm/mm

2. n = 0.013 (for new concrete/PVC pipe)

Sample Calculation (for Line 1):

Cumulative flow = 67375+1821679 lpd

= 1889054/(24*60*60*1000) m3/s

= 0.022 m3/s

Pipe slope, s = 0.003

Using Manning’s equation,

Exact diameter of pipe, DExact = 1.548 [(0.013 * 0.022)/√0.003]0.375mm

= 215 mm

Provided pipe diameter, DActual = 250 mm

Check for Velocity:

Used Formula:

Qfull = (𝐷/1.548)(1/0.375)*(√𝑠/𝑛)

Here,

Qfull= Full Flow

D = Actual Diameter

s = Slope

Vfull = (1/𝑛)∗(𝐷/4)(2/3)∗𝑠(1/2)

Assumptions:

1. s is assumed 0.00 in/in

2. n = 0.013 (for new concrete/PVC pipe)

3. Figure 3 is used to calculate d/D and v/Vfull from Q/Qfull.

Sample Calculation (for Line 1):

Here,

D = 250 mm

s= 0.003 mm/mm

n = 0.013

So, Qfull = (((250/1000)*1.548)(1/0.375))*(√(0.003)/0.013)

= 0.033 m3/s

So, Q/ Qfull = 0.67

From Hydraulic element diagram Fig: 08

For, Q/ Qfull = 0.67 ; V/Vfull = 0.94

d /D = 0.7

Vfull= (1/ 0.013)*((250/1000)/4)(2/3))*(0.003)(1/2)

=0.66 m/s

So, V = 0.62 which is greater than 0.6 and smaller than 3. So, it is OK.

Check for Cover:

Sample Calculation (for Line 1):

Here,

Length = 170 m

Slope = 0.003 (from Table 3)

Diameter = 250 mm

Fall in Sewer = 170X.003 = .51 m

Invert Drop = 0

Ground Elevation = 28.48 m (Upper End), 28.05 m (Lower End)

Sewer Invert Elevation:

Upper End = (28.48 -2-0.05-0.250) m = 26.18 m

Lower End = 26.18 -170*0.003 = 25.67 m

So, Cover at upper end = (28.48 -26.18 -0.250-0.05) m = 2 m

Cover at lower end = (28.05 -25.67 -0.25-0.05) m = 2.1 m

Table 6-1: Description of Contribution Areas, Node Numbers for Trunk Sewer:

Table 6-4: Pipe Diameter Calculation for Trunk Sewer:

Table 6-5: Check for Sewer pipe Cover:

Table 6-6: Location of Manholes:

Reference Tables & Figures:

Figure 6-1: Average Infiltration Rate Allowance for New Sewers

[Note: ha x 2.4711= acre;  m3/ha·d x 106.9 = gal/acre·d]

Figure 6-2: Peaking Factor for Residential Wastewater Flows

Figure 6-3: Hydraulic Element Diagram

Table 6-7: Percentage of Avg. Water Demand to consider as Avg. Waste Water Generation

Table 6-8: Peak Factors for Different Facilities

Table 6-9: Gravity Sewer Minimum Pipe Slopes

Chapter 7

Chapter 8

Objective:

The objective of this assignment is to design the building drainage system of a typical building which is a integral part of the building’s Plumbing System.

Introduction:

A drainage system (drainage piping) includes all the piping within public or private premises, which conveys sewage, rain water, or other liquid wastes to a legal point of disposal, but does not include the mains of a public sewer system or a private or public sewage treatment or disposal plant.

Major Elements of Building Drainage System:

Wastewater drainage pipe:

Soil stack,

waste stack and

vent pipes,

Building drains and building sewers, including connections, devices, and appurtenances

within the property lines of the premises

Design Considerations:

The waste branch from bath room, wash basin or sink should be of 32 mm to 50 mm

diameter and should be trapped immediately beneath such wash basins or sink by an

efficient siphon trap with adequate means of inspection and cleaning.

The minimum recommended size of waste stack is 75 mm

The soil and waste stack should be continued upward undiminished in size 0.6 m above

the roof surface when the roof will be used only for weather protection. Where the roof

will be used for any purpose other than weather protection, the soil and vent stack

should run at least 2 m above the roof surface to ensure least possible nuisance.

The soil and waste stack should be firmly attached to the wall with a minimum

clearance of25 mm from the wall

The diameter of a vent stack should not be less than 50 mm

The diameter of a branch vent pipe on a waste pipe should not be less than 25

mm or two-thirds of the diameter of the branch waste pipe ventilated.

The branch vent pipe on a soil pipe should be at least 32 mm in diameter

An relief vent should be at least one-half the size of the drain it vents (no less

than 1 1/4", 32 mm)

All vent stacks should extend undiminished in size above the roof or should be

reconnectedto a vent header or to the stack vent portion of the soil or waste

stack, at least 150 mm above the flood level of the highest fixture connection

discharging into the soil or waste stack. Where the roof is to be used for any

purpose other than weather protection, the ventextension should be in

accordance with as stated earlier in this topic

The soil pipe conveying any solid or liquid filth to a sewer drain should be circular

with a minimum diameter of 100 mm

Slopes:

Horizontal drainage piping of 75 mm diameter and less is to be installed with a fall

of not less than 20 mm per m.

Horizontal drainage piping larger than 75 mm diameter need to be installed with a

fall of notless than 10 mm per m

It is a good policy to design the system for the highest possible velocity. However,

velocities in pipes with slopes greater than 20 mm per m may cause self-

siphonage of trap seal

Design Steps:

1. Designing “Two pipe drainage system “.

2. Estimating the total load weight (DFU) carried by a soil or waste pipe, the relative load

weight for different kinds of fixtures use Table 8.6.14. Table 8.6.15provides an

approximate rating of those fixtures not listed in Table 8.6.14.

3. Slope: Designing the building drains and sewer to discharge the peak simultaneous load

weight  flowing half-full with a minimum self-cleansing velocity of 0.75 m per second.

However, flatter gradient may be used if required but the minimum velocity should not

be less than 0.6 m per second. Again, it is undesirable to employ gradients giving a

velocity of flow greater than 2.5 m per second.

4. The maximum number of fixture units that may be connected to a given size of building

sewer, building drain, horizontal branch or vertical soil or waste stack should be as

providedin Tables 8.6.16and 8.6.17. Using the load factor unit as obtained in step-1,

calculate size of horizontal branches or vertical soil or waste stack(s) from Table-8.6.16   If

branches are not too long we provided 65 mm all through.

In the same way we determined soil/waste stack diameter depending on total number of

branches connecting to that part of the stack and number of story in the building.

5. Vents are normally sized by using the "Developed Length" (total linear footage of pipe

making up the vent) method. Determining the size of vent piping from its length and the

total of the fixture units connected in accordance with Table 8.6.21 ( from supplied

documents)

6. Determining the branch vent size using Table 8.6.22 ( from supplied documents)

# Drainage System Design

Assumptions:

- Soil stack conveys discharge of water closet.

- Waste stack conveys   discharge of   shower, Sink, Wash basin ,ablution Tap etc.

- Vent stack is continued over 2m from roof.

- The whole building is divided into 2 part each having 9 units.

- One soil stack, one waste stack and one vent stack is provided for 9 apartments.

Design of   Waste  Stack& Soil Stack

Waste Stack Design:

DFU calculation of Each apartment,

- wash basin=3

- ablution tap=1

- shower	=3

- kitchen sink=1

The load factor of different unit is (table 8.6.14)

- wash basin-1

- ablution tap-1

- shower-2

- kitchen sink-2

So, total DFU for an apartment is =3*1+1*1+

3*2+1*2=12

So, total DFU of 9 apartments =12*9=108

From, table 8.6.16- diameter of waste stack is 100 mm

From, table 8.6.17- slope of waste stack is 0.01

Waste Stack Design:

Branch stack:

For Any Storey:

Branch of waste stack in East and West face:

- wash basin=2

- shower	=2

The load factor of different unit is (table 8.6.14)

- wash basin-1

- shower-2

So, total DFU for an apartment is =2*1+2*2=6

From, table 8.6.16- diameter of waste stack is 50mm

Branch of waste stack in North and South face:

- wash basin=1

- ablution tap=1

- shower	=1

- kitchen sink=1

The load factor of different unit is (table 8.6.14)

- wash basin-1

- ablution tap-1

- shower-2

- kitchen sink-2

So, total DFU for an apartment is =1*1+1*1+1*2+1*2=6

So, Diameter of waste stack is 50mm(from table 8.6.16)

Soil Stack Design:

DFU of each apartment;

- Water closet=3

- Load factor of water closet =3

So, total DFU for an apartment is=3*3=9

So, total DFU of 9 apartments =9*9=81

So, Diameter of soil stack is 100 mm (from  table 8.6.16)

So, Slope of soil stack is 0.01 (from table 8.6.17)

Design of vent stack:

Total FU including both soil & waste stack=189 (9 apartments)

Diameter of soil/waste stack 100 mm

Maximum Developed length of vent stack=90+10=100’=30.48m

From table 8.6.21-Diameter of Vent Stack=75 mm

Design of Vent Pipe

Reference Tables & Figures:

Chapter 7

Objective:

The objective of this report is to design Down Feed Water Supply System of a building with an overhead and underground water reservoir.

Introduction:

The plumbing includes the practice, materials, and fixtures used in the installation., maintenance, extension, and alteration of all piping, fixtures, appliances, and accessories in connection with sanitary drainage or storm drainage facilities, the venting system and the public or private water supply systems/ within or adjacent to any building, structure, or conveyance. For water supply purpose we use water supply and distribution pipes: riser, up feed or down feed distribution pipes, underground water reservoir (UGWR), overhead (OH) tank.

Design Components:

1. Sizing of Water Distribution Pipes within the Building

2. Dimensions of UGWR

3. Dimensions of OH tank

4. Determination of size of riser

Procedure:

1. Sizing of Water Distribution Pipes within the Building

2. Calculation of Dimension of Underground Water Reservoir

3. Calculation of Dimension of Overhead Water Tank

4. Calculation of Dimension of Overhead Water Tank

5. Design of Riser Pipe and Pump

6. Calculation of pump capacity

Fixture Unit calculation : ( Using Table 8.5.4 & Table- P-1)

| Location | Type of Fixture | No of Fixture | FU | Total FU | Sum | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Toilet (4’-4’’X7’4’’) | 1.Wash basin | 1 | 2 | 2 | 10 | 29 |
|  | 2.Shower | 1 | 2 | 2 |  |  |
|  | 3.Water closet | 1 | 5 | 5 |  |  |
|  | 4.Ablution tap | 1 | 1 | 1 |  |  |
| Toilet (5’-1’’X4’-6’’) | 1.Wash basin | 1 | 2 | 2 | 10 |  |
|  | 2.Shower | 1 | 2 | 2 |  |  |
|  | 3.Water closet | 1 | 5 | 5 |  |  |
|  | 4.Ablution tap | 1 | 1 | 1 |  |  |
| Toilet (6’X4’-6’’) | 1.Wash basin | 1 | 2 | 2 | 7 |  |
|  | 2.Water closet | 1 | 5 | 5 |  |  |
| Kitchen | 1.Sink | 1 | 2 | 2 | 2 |  |

FU per unit = 29

It’s a 9 story building and 2 unit per story = 9X2= 18 unit

In addition a car wash = 6 FU

Total WSFU = 18X29+6 = 528

Underground Water Reservoir Design

Since the area of the apartment is 922 SFT (<1500 SFT) From Table 8.5.1(a)

Water consumption = 135 lpcd ( Category b1, Restricted facility)

In drivers room assuming 10 beds

Water consumption = 80 lpcd (Table 8.5.1(a), category c1)

Assuming 6 members per family

Total water requirement = 135X6X18 + 80X10 =15380 lpd

With 1 day extra capacity

Capacity of the underground reservoir = 15380X2 = 30760 liter

= 1085.5 cft

Stair room surface area = 16X8 =128 sft

Height of UGWR = 1085.5/128 = 8.48 =8.5’

Taking 1’ as a freeboard

Dimensions of UGWR = 16’X8’X9.5’

Over Hand Tank Design

Total water requirement =15380 lpd (from UGWR calculation)

Assuming  two times pumping a day ( 1hr each)

Volume needed = 15380/2 = 7680 litre

Fire fighting water requirement = 1000 l/min (from table 4.4.1 , Light Hazard 1)

= 1000X30

= 30000 litre

So, total volume of OHT =7680+30000 = 37860 litre

= 1330 cft

If thickness of the wall of OHT is 10’’ area available= (8’-.83’)X(16’-.83’)

= 108 sft

So, Height of OHT =1330/108

=12.31ft

Considering 1’ freeboard

Dimensions of OHT = 7’-2’’X15’-2’’X13.5’

Riser Pipe Design

Water carried by the riser during each time of pumping

=  7680 litre/pumping hr

= 7680/3.28/60 gpm

= 33.86 = 34 gpm

Let , velocity  v = 10 fps

So, pipe diameter = 1.2’’ = 1.5 ‘’ (from figure P4)

Head loss = 15 psi /100’ (from figure P4)

Pump Capacity Calculation

Total   length of riser (L) = total building height (10 ft per floor) + 10’ from UGWR + OH tank inlet height above top roof surface.

= 10X9 +10 + (13.5’+ 15’)

= 128.5’

Total frictional head , HL = (hL*L/100) + 8 + 5

= ( 15X128.5/100) + 8 +5

=32.3 psi

= 74.5’

Velocity head     = V2/2g

= (102/2*32.2)’

= 1.55’

Total Head = 74.5+1.55+128.5 =204.55’

Pump capacity = HQ/(3960E)

= 204.55X34/3960/.6   (assuming E=60%)

=2.93 hp

= 3hp

Design of Down Feed Pipe Size

We divide the whole building in two zone

- Zone 1 ( 9,8,7,6th floor)

- Zone 2 (5,4,3,2,1st floor0

For top floor:

FU per floor = 58

So, Accumulated FU = 4X58 = 232

Water demand = 280 litre/min (From Fig: P1)

= 74 gpm

Total pipe length from tank to 9th floor (vertical length)

=20’+3’( Height of OHT=20’, 3’ for top floor)

= 23’

Let , Fittings 1 tee and 6 elbow

Equivalent length = 1x2.50 + 6x1.53 = 11.68 mm

= .04’ = .1’

Horizontal pipe length from layout = 52.5’

Total horizontal pipe length = 52.5+.1 = 52.6’

Let,

- Minimum pressure at fixture = 8 psi

- Fixture branch pressure = 1 psi

Equivalent pipe length = 52.6+23 =75.6’

Available pressure loss = P +.434(h)-f

= 0+.434x23-8-1

= 1 psi

Available pressure loss = 1*100/75.6 =1.31 psi/100’

From Fig: P5

Diameter of vertical pipe = 3’’

| Determination of Down feed Pipe Size |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Zone | Storey | Fixture Unit | Accumulated Fixture Unit | Water Demand | Vertical Length | Available Pressure Loss | Horizontal Pipe Length | Fittings Length | Total Equivalent Length | Available Pressure Drop | Pipe Size |
|  |  | FU | FU | gpm | ft | psi | ft | ft | ft | psi/100' | inch |
| 1 | 9 | 58 | 232 | 74.0 | 23 | 1 | 52 | 0.1 | 75.1 | 1.31 | 3 |
|  | 8 | 58 | 174 | 60.7 | 33 | 5 | 52 | 0.1 | 85.1 | 6.25 | 2 |
|  | 7 | 58 | 116 | 50.2 | 43 | 10 | 52 | 0.1 | 95.1 | 10.16 | 1.5 |
|  | 6 | 58 | 58 | 31.7 | 53 | 14 | 52 | 0.1 | 105.1 | 13.32 | 1.5 |
| 2 | 5 | 58 | 290 | 79.3 | 63 | 18 | 52 | 0.1 | 115.1 | 15.94 | 1.5 |
|  | 4 | 58 | 232 | 74.0 | 73 | 23 | 52 | 0.1 | 125.1 | 18.13 | 1.5 |
|  | 3 | 58 | 174 | 60.7 | 83 | 27 | 52 | 0.1 | 135.1 | 20.00 | 1.5 |
|  | 2 | 58 | 116 | 50.2 | 93 | 31 | 52 | 0.1 | 145.1 | 21.61 | 1.5 |
|  | 1 | 58 | 0 | 31.7 | 103 | 36 | 52 | 0.1 | 155.1 | 23.02 | 1.5 |