Fixture Unit calculation : ( Using Table 8.5.4 & Table- P-1)

| Location | Type of Fixture | No of Fixture | FU | Total FU | Sum | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Toilet (4’-4’’X7’4’’) | 1.Wash basin | 1 | 2 | 2 | 10 | 29 |
|  | 2.Shower | 1 | 2 | 2 |  |  |
|  | 3.Water closet | 1 | 5 | 5 |  |  |
|  | 4.Ablution tap | 1 | 1 | 1 |  |  |
| Toilet (5’-1’’X4’-6’’) | 1.Wash basin | 1 | 2 | 2 | 10 |  |
|  | 2.Shower | 1 | 2 | 2 |  |  |
|  | 3.Water closet | 1 | 5 | 5 |  |  |
|  | 4.Ablution tap | 1 | 1 | 1 |  |  |
| Toilet (6’X4’-6’’) | 1.Wash basin | 1 | 2 | 2 | 7 |  |
|  | 2.Water closet | 1 | 5 | 5 |  |  |
| Kitchen | 1.Sink | 1 | 2 | 2 | 2 |  |

FU per unit = 29

It’s a 9 story building and 2 unit per story = 9X2= 18 unit

In addition a car wash = 6 FU

Total WSFU = 18X29+6 = 528

Underground Water Reservoir Design

Since the area of the apartment is 922 SFT (<1500 SFT) From Table 8.5.1(a)

Water consumption = 135 lpcd ( Category b1, Restricted facility)

In drivers room assuming 10 beds

Water consumption = 80 lpcd (Table 8.5.1(a), category c1)

Assuming 6 members per family

Total water requirement = 135X6X18 + 80X10 =15380 lpd

With 1 day extra capacity

Capacity of the underground reservoir = 15380X2 = 30760 liter

= 1085.5 cft

Stair room surface area = 16X8 =128 sft

Height of UGWR = 1085.5/128 = 8.48 =8.5’

Taking 1’ as a freeboard

Dimensions of UGWR = 16’X8’X9.5’

Over Hand Tank Design

Total water requirement =15380 lpd (from UGWR calculation)

Assuming  two times pumping a day ( 1hr each)

Volume needed = 15380/2 = 7680 litre

Fire fighting water requirement = 1000 l/min (from table 4.4.1 , Light Hazard 1)

= 1000X30

= 30000 litre

So, total volume of OHT =7680+30000 = 37860 litre

= 1330 cft

If thickness of the wall of OHT is 10’’ area available= (8’-.83’)X(16’-.83’)

= 108 sft

So, Height of OHT =1330/108

=12.31ft

Considering 1’ freeboard

Dimensions of OHT = 7’-2’’X15’-2’’X13.5’

Riser Pipe Design

Water carried by the riser during each time of pumping

=  7680 litre/pumping hr

= 7680/3.28/60 gpm

= 33.86 = 34 gpm

Let , velocity  v = 10 fps

So, pipe diameter = 1.2’’ = 1.5 ‘’ (from figure P4)

Head loss = 15 psi /100’ (from figure P4)

Pump Capacity Calculation

Total   length of riser (L) = total building height (10 ft per floor) + 10’ from UGWR + OH tank inlet height above top roof surface.

= 10X9 +10 + (13.5’+ 15’)

= 128.5’

Total frictional head , HL = (hL*L/100) + 8 + 5

= ( 15X128.5/100) + 8 +5

=32.3 psi

= 74.5’

Velocity head     = V2/2g

= (102/2*32.2)’

= 1.55’

Total Head = 74.5+1.55+128.5 =204.55’

Pump capacity = HQ/(3960E)

= 204.55X34/3960/.6   (assuming E=60%)

=2.93 hp

= 3hp

Design of Down Feed Pipe Size

We divide the whole building in two zone

- Zone 1 ( 9,8,7,6th floor)

- Zone 2 (5,4,3,2,1st floor0

For top floor:

FU per floor = 58

So, Accumulated FU = 4X58 = 232

Water demand = 280 litre/min (From Fig: P1)

= 74 gpm

Total pipe length from tank to 9th floor (vertical length)

=20’+3’( Height of OHT=20’, 3’ for top floor)

= 23’

Let , Fittings 1 tee and 6 elbow

Equivalent length = 1x2.50 + 6x1.53 = 11.68 mm

= .04’ = .1’

Horizontal pipe length from layout = 52.5’

Total horizontal pipe length = 52.5+.1 = 52.6’

Let,

- Minimum pressure at fixture = 8 psi

- Fixture branch pressure = 1 psi

Equivalent pipe length = 52.6+23 =75.6’

Available pressure loss = P +.434(h)-f

= 0+.434x23-8-1

= 1 psi

Available pressure loss = 1*100/75.6 =1.31 psi/100’

From Fig: P5

Diameter of vertical pipe = 3’’