Calculation of Wastewater entering each line:

Assumptions:

1. Percentage of average water demand taken from Table 1

2. Peak factors for different facilities taken from Table 2

3. Peak factors for Residential zone taken from Figure 2

Sample Calculation (for line 1):

For Contributing Area A1

Area description: Shopping Mall, Bazar, Convention Hall, First Class and Second Class Quarter, Chairman Bungalow, Mosque, Day Care Center, Swimming Pool, School & College, Playground, Water Pumping Station

Average Demand:Residential=413280 lpd,Commercial= 101376

lpd, Industrial 0 lpd, Institutional 231984

lpd

Average Wastewater:

Average Wastewater= (0.75*413280+0.75*101376+0.9*0+0.70*231984) lpd

= 548381 lpd

Peak Wastewater:

Peak Wastewater = (3.34*0.75*413280 + 1.8*0.75*101376

+2.1*0.9*0+4*0.75*231984) lpd

= 1821679 lpd

Calculating the amount of Wastewater:

Assumptions:

- Average infiltration rate is taken from Figure 1

Sample Calculation (for line 1):

For Contributing Area A1

Total Area = 7.7 ha

Average Infiltration Rate = 8.75 m3/ha.d

Infiltration and Inflow = 7.7 *8.75*1000lpd = 67375 lpd

Calculating the Diameter of the Pipe:

Used Formula:

- Manning’s Equation

D= 1.548*(𝑛𝑄/√s)0.375

Here,

D = Diameter of the Pipe

s = Slope of the Pipe

Q = Cumulative flow

Assumptions:

1. s is assumed 0.005 mm/mm

2. n = 0.013 (for new concrete/PVC pipe)

Sample Calculation (for Line 1):

Cumulative flow = 67375+1821679 lpd

= 1889054/(24*60*60*1000) m3/s

= 0.022 m3/s

Pipe slope, s = 0.003

Using Manning’s equation,

Exact diameter of pipe, DExact = 1.548 [(0.013 * 0.022)/√0.003]0.375mm

= 215 mm

Provided pipe diameter, DActual = 250 mm

Check for Velocity:

Used Formula:

Qfull = (𝐷/1.548)(1/0.375)*(√𝑠/𝑛)

Here,

Qfull= Full Flow

D = Actual Diameter

s = Slope

Vfull = (1/𝑛)∗(𝐷/4)(2/3)∗𝑠(1/2)

Assumptions:

1. s is assumed 0.00 in/in

2. n = 0.013 (for new concrete/PVC pipe)

3. Figure 3 is used to calculate d/D and v/Vfull from Q/Qfull.

Sample Calculation (for Line 1):

Here,

D = 250 mm

s= 0.003 mm/mm

n = 0.013

So, Qfull = (((250/1000)*1.548)(1/0.375))*(√(0.003)/0.013)

= 0.033 m3/s

So, Q/ Qfull = 0.67

From Hydraulic element diagram Fig: 08

For, Q/ Qfull = 0.67 ; V/Vfull = 0.94

d /D = 0.7

Vfull= (1/ 0.013)*((250/1000)/4)(2/3))*(0.003)(1/2)

=0.66 m/s

So, V = 0.62 which is greater than 0.6 and smaller than 3. So, it is OK.

Check for Cover:

Sample Calculation (for Line 1):

Here,

Length = 170 m

Slope = 0.003 (from Table 3)

Diameter = 250 mm

Fall in Sewer = 170X.003 = .51 m

Invert Drop = 0

Ground Elevation = 28.48 m (Upper End), 28.05 m (Lower End)

Sewer Invert Elevation:

Upper End = (28.48 -2-0.05-0.250) m = 26.18 m

Lower End = 26.18 -170*0.003 = 25.67 m

So, Cover at upper end = (28.48 -26.18 -0.250-0.05) m = 2 m

Cover at lower end = (28.05 -25.67 -0.25-0.05) m = 2.1 m