Summary of Grain Size Distribution Curve:

| Depth (ft) | FM | D10 (mm) | D30 (mm) | D60 (mm) | Cu | Silt/Clay (%) | Fine Sand (%) | Medium Sand (%) | Course Sand (%) | Fine Gravel (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 250-300 | 1.3 | .14 | .21 | .3 | 2.18 | 0 | 28.1 | 68.8 | 3.1 | 0 |
| 300-360 | 1.7 | .19 | .3 | .39 | 2.09 | 0 | 12.17 | 83.73 | 4.1 | 0 |
| 360-370 | 1.45 | .15 | .23 | .34 | 2.29 | 0 | 22.53 | 75.17 | 2.3 | 0 |
| 370-400 | 1.71 | .19 | .29 | .37 | 1.98 | 0 | 12.3 | 81.9 | 5.8 | 0 |
| 400-420 | 1.52 | .18 | .24 | .34 | 1.93 | 0 | 17.4 | 81.2 | 1.4 | 0 |
| 420-460 | 1.79 | .18 | .27 | .39 | 2.13 | 0 | 14.03 | 76.99 | 5.17 | 3.63 |

Well Casing Pipe Length:

Existing water table=280’

Water level declination=2’/year

Design period = 20 years

Total declination of water level = 20*2' = 40'

Let drawdown=15’

F.S. =15’

So, length of casing pipe = (280+40+15+15) =350’

Since bore log ends at 460’

We take length of casing pipe=460’

Strainer Location and Length:

Minimum depth of strainer=280+40+15+15=350’

So Strainer may be provided between 360’ – 450’

Depth of Acquifer =180’

Available Depth= 460 - 350=110’>50’

Length of Strainer=.8x110=88’

We take Strainer length of 90’ (360’-450’)

Selection of Strainer slot no:

Slot Number = Slot size (in mm) x 1000 / 25.4

D10 of Gravel Pack= .85mm

Slot number= .85*1000/25.4=33.5

Let us take Slot size 30

Strainer dia 6’’

Gravel Pack Design:

From depth 360’-450’

F.M. lowest  =1.52

Multiplication factor= 5

D30 at Depth 400-420ft =.24 mm

D30 of gravel pack =.24*5=1.2 mm

Cu of gravel pack= 2.11 <2.5 (O.K.)

4 inch diameter envelop of gravel pack material will surround the

entire screen.

Yield Calculation

Yield of one well = Area*velocity*Screen blockage factor

Let

Velocity is 0.1 fps

Screen blockage 0.4

Diameter 0.5’

16hrs. Pumping hour

Yield= (π*.5*90*.15*.1*.4) =.848 ft3/sec= (.848*.30483*1000*3600) lph= 86469.12 lph

As pumping is done for 18hrs a day, total yield per day = 86469.12×18 lpd

=  1556444.16 lpd

| Water Demand Summary |  |  |  |
| --- | --- | --- | --- |
| Zones | Present water Demand (lpd) | Demand after 10 years (lpd) | Demand after 20 years (lpd) |
| Residential | 724450 | 799250 | 880800 |
| Industrial | 497805 | 705211.5 | 906391.5 |
| Commercial | 1051837.8 | 1157357.2 | 1262876.6 |
| Fire Fighting | 86550 | 95010 | 102570 |
| Total | 2360642.8 | 2756828.7 | 3152638.1 |

Number of tube wells:

Residential area + Commercial area

| Time | Water demand (lpd) | Number of tube wells required |
| --- | --- | --- |
| Present | 1776288 | 2 |
| After 10 years | 1956607 | 2 |
| After 20 years | 2143677 | 2 |

Industrial Zone

| Time | Water demand (lpd) | Number of tube wells required |
| --- | --- | --- |
| Present | 497805 | 1 |
| After 10 years | 705211 | 1 |
| After 20 years | 906391 | 1 |