Water Demand Calculation

• Water requirement can be calculated

1. Residential water demand.

2. Industrial water demand.

3. Water demand for commercial services.

4. Water demand for fire fighting

Reference

- Occupancy types are set according to BNBC 2006 (table8.5.1(a))

- Water demand is set according to BNBC 2006 (table8.5.1(d))

Peak factors:

Residential zone = 2.4

Industrial zone = 1.4

Administrative zone = 1.4

Common Facility zone = 4

Fire Fighting = 1

Water Demand for Residential zone:

| Residence Type | Present Population | Per Capita Consumption,lpcd | Duration,hrs | Average Present Demand,lpd | Peak Factor | Time Factor | Peak Present Demand,lpd | Population After 10 Years | Avg. Demand After 10 Years,lpd | Peak Demand After 10 Years | Population After 20 Years | Avg. Demand After 20 Years,lpd | Peak Demand After 20 Years.lpd |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Chairman Bungalow | 12 | 260 | 24 | 3120 | 2.5 | 1 | 7800 | 13 | 3380 | 8450 | 14 | 3640 | 9100 |
| 1st Class Officers Residence | 336 | 200 | 24 | 67200 | 2.5 | 1 | 168000 | 364 | 72800 | 182000 | 395 | 79000 | 197500 |
| 2nd Class Officers Residence | 472 | 120 | 24 | 56640 | 2.5 | 1 | 141600 | 522 | 62640 | 156600 | 576 | 69120 | 172800 |
| 3rd Class Employees Dorm | 265 | 100 | 24 | 26500 | 2.5 | 1 | 66250 | 296 | 29600 | 74000 | 330 | 33000 | 82500 |
| 4th Class Dorm | 1204 | 80 | 24 | 96320 | 2.5 | 1 | 240800 | 1344 | 107520 | 268800 | 1500 | 120000 | 300000 |
| Doctors Quarter | 125 | 200 | 24 | 25000 | 2.5 | 1 | 62500 | 136 | 27200 | 68000 | 147 | 29400 | 73500 |
| Teachers Quarter | 125 | 135 | 24 | 16875 | 2.5 | 1 | 42187.5 | 136 | 18360 | 45900 | 147 | 19845 | 49612.5 |
| Babies Day Care | 60 | 180 | 12 | 10800 | 2.5 | 2 | 27000 | 60 | 10800 | 27000 | 60 | 10800 | 27000 |
| Total | 2599 | 1275 | 180 | 302455 | 20 | 9 | 756138 | 2871 | 3660525 | 830750 | 3169 | 364805 | 912013 |

Water Demand For Industrial Zone

Assumption:

- Per day production is asuumed as 10000lb/day

- Water requirement 1.8 L/lb (source:http://www.yarnsandfibers.com/preferredsupplier/reports_fullstory.php?id=475&section=&p_type=General&country=Global)

| Industrial Water Demand Calculation |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Use for Industrial Production |  |  |  |  |  |  |  |  |
| Present Production Rate(lb/d) | Future Production Rate(lb/d) |  | Water Requirement forProduction(litre per lb) | PF | TF | Present Water Demand(lpd) | Future Water Demand(lpd) |  |
|  | After 10 years | After 20 years |  |  |  |  | After 10 years | After 20 years |
| 10000 | 15000 | 20000 | 1.8 | 1.4 | 1.5 | 37800 | 56700 | 75600 |

| Water Use for Personal Consumption |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Building Description | Occupancy Type | total Workers at Present | Total Workers |  | PF+TF | Per CapitaConsumption(lpcd) | Present Water Demand(lpd) | Future Water Demand(lpd) |  |  |
|  |  |  | After 10 years | After 20 years |  |  |  | After 10 years | After 20 years | Remarks |
| Knitting | G1 | 161 | 186 | 202 | 2.9 | 25 | 11672.5 | 13485 | 14645 | Two Shifts 8hrs so TF=24/16=1.5 |
| Weaving |  | 161 | 186 | 202 | 2.9 | 25 | 11672.5 | 13485 | 14645 |  |
| Washing |  | 191 | 220 | 240 | 2.9 | 25 | 13847.5 | 15950 | 17400 |  |
| Storing(textile) |  | 104 | 120 | 130 | 2.9 | 25 | 7540 | 8700 | 9425 |  |
| Raw Material Storage |  | 50 | 58 | 63 | 2.9 | 25 | 3625 | 4205 | 4567.5 |  |
| Spinning |  | 191 | 220 | 240 | 2.9 | 25 | 13847.5 | 15950 | 17400 |  |
| Dyeing |  | 176 | 203 | 220 | 2.9 | 25 | 12760 | 14717.5 | 15950 |  |
| Finishing (textile) |  | 119 | 137 | 150 | 2.9 | 25 | 8627.5 | 9932.5 | 10875 |  |
| Sewing |  | 191 | 220 | 240 | 2.9 | 25 | 13847.5 | 15950 | 17400 |  |
| Cutting |  | 191 | 220 | 240 | 2.9 | 25 | 13847.5 | 15950 | 17400 |  |
| Heavy Vehicle Parking Place |  | 10 | 12 | 13 | 2.9 | 25 | 725 | 870 | 942.5 |  |
| Printing |  | 191 | 220 | 240 | 2.9 | 25 | 13847.5 | 15950 | 17400 |  |
| Finishing(apparel) |  | 101 | 117 | 127 | 2.9 | 25 | 7322.5 | 8482.5 | 9207.5 |  |
| Storing (apparel) |  | 108 | 125 | 135 | 2.9 | 25 | 7830 | 9062.5 | 9787.5 |  |
| ETP |  | 25 | 29 | 32 | 2.9 | 25 | 1812.5 | 2102.5 | 2320 |  |
| Waste Dumping |  | 10 | 12 | 13 | 2.9 | 25 | 725 | 870 | 942.5 |  |
| Parking Space & Heavy Vehicle parking space | K1 | 10 | 10 | 10 | 2.4 | 5 | 120 | 120 | 120 |  |
| Admin building | F1 | 250 | 288 | 313 | 2.9 | 30 | 21750 | 25056 | 27231 |  |
| Total |  | 2240 | 2583 | 2810 | 51.7 | 435 | 165420 | 190839 | 207659 |  |

Water requirement for fire fighting

Assumptions for Calculating Fire Hydrant Water Demand:

1Each point must be served by at least two fire hydrants at a time

Nozzle diameter of the hydrant is 3 inches (2r)

Velocity of water in the pipe is 3 fps (v)

Each hydrant will supply water for 30 minutes (t)

| Water Demand for Fire Fighting |  |  |  |  |
| --- | --- | --- | --- | --- |
| Diameter of the Hydrant (inch) | Velocity Required(fps) | Flow Time (min) | Volume of water in One Hydrant (litre) | Volume of water in Two Hydrant (litre) |
| 3 | 3 | 30 | 7510 | 15020 |

| Water Demand Summary |  |  |  |
| --- | --- | --- | --- |
| Zones | Present water Demand (lpd) | Demand after 10 years (lpd) | Demand after 20 years (lpd) |
| Residential | 756138 | 830750 | 912013 |
| Industrial | 203220 | 247538.5 | 283258.5 |
| Commercial | 1014398 | 1115837 | 1217277 |
| Fire Fighting | 15020 | 15020 | 15020 |
| Total | 1988776 | 2209145.5 | 2427568.5 |