Objective:

The objective of this report is to calculate pump capacity and prepare a pumping schedule of an industrial village.

Introduction:

In order to meet the water demand of our industrial village, we need to find pump capacity. In this report pump capacity is calculated in Horse-power (HP) unit . Also pump schedule is designed, accordingly pumps will be installed and operated for a period of 20 years.

Used Formula:

1. Working Horse Power, WHP = HQ/3960

H = Total head of the pump (ft.)

Q = Yield of well (gpm)

2. Breaking Horse Power, BHP = WHP/ ƞ

ƞ = Pump Efficiency

3. Total Head, H = Static head + Velocity head + Friction head

4. Static head = Suction head + Delivery head

5. Total Delivery Head = Static Water Level + Maximum Building Height

6. Velocity head = v2/2g

7. Maximum Pipe Length = Maximum horizontal distance + Maximum height of building + Height of overhead tank

Assumptions:

1. ƞ is assumed to be 75%.

2. We will use submersible pump, So suction head = 0

3. Friction loss is assumed to be 10% of total pipe length.

4. Height of floor is 10 ft.

5. Velocity is assumed 3 fps.

6. Height of overhead tank is assumed 12’

Sample Calculation:

For Pump 1

Pump capacity:

Static Head = Suction Head (hs) + Delivery Head (hd)

Here Suction head = 0 (Submersible Pump)

Delivery head,

hd  = Static water level + Maximum building height

= 280’+60’ +12’= 352’

Velocity head,

hv = v2/ 2g = 32/(2*32) =0.14’

Friction head,

Maximum pipe length = Maximum horizontal distance + Maximum height of the building

+ Height of overhead tank

= 496’+60’+12’ = 568’

Friction Head = Maximum pipe length* 10%

= 568*0.1 = 56.8’

So, Total head,

H = static head+ velocity head+ friction head

= 352’+.14’+56.8’

= 408.94’

Yield of well,

Q = 64851.84 lph

= 64851.84 /227.13

= 285.53 gpm

WHP = HQ/3960

= (408.94*285.53)/3960

= 29.49 HP

Let, Pump Efficiency  = 75%

BHP = WHP/.75

= 28.65 /0.75

=39.32 HP

|  | Pump | Yield Q gpm | Maximum Horizontal distance Ft | hs ft | hd ft | hv ft | hf Ft | H ft | WHP hp | BHP hp |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Residential & Commercial | P3 | 285.53 | 606 | 0 | 352 | 0.14 | 67.8 | 419.9 | 30.3 | 40.4 |
|  | P2 | 285.53 | 285 | 0 | 352 | 0.14 | 35.7 | 387.8 | 28 | 37.3 |
| Industrial | P1 | 285.53 | 496 | 0 | 352 | 0.14 | 56.8 | 408.9 | 29.5 | 39.3 |