## Sheet1
1.Residential Water Demand
| Occupancy Type | Present Member | Future Provition | Per Capita Consumption (LCPD) | present water Demand (LPD) | Future Water Demand |  | Remarks
[6 empty] | After 10 Years (LPD) | After 20 Years (LPD) | [7 empty] | 1.8114 | 38038.5933 | 121977.0891
MD's and Guest House | A1 | 10 | 1 | 400 | 4000 | 4418.4885 | 4880.7602 |  | 4418.4885 | 4880.7602 | 5391.3957
1st Class Officers' Residence | A2 | 400 | 1.5 | 225 | 90000 | 104448.6743 | 121216.9506 | 1st Class Officers = 80 Assume,Family Members=5 (avg) | 104448.6743 | 121216.9506 | 140677.2198
2nd Class Officers' Residence | A2 | 1770 | 2.5 | 135 | 238950 | 305876.2018 | 391547.3984 | 2nd Class Officers = 295 Assume,Family Members=6 (avg) | 305876.2018 | 391547.3984 | 501213.773
Bachelors' Residence | A4 | 1045 | 2 | 70 | 73150 | 89169.4418 | 108697.052 |  | 89169.4418 | 108697.052 | 132501.0999
Dormetory | A3 | 300 | 2 | 70 | 21000 | 25598.8828 | 31204.8953 |  | 25598.8828 | 31204.8953 | 38038.5933
| Total Residential Water Demand |  |  |  | 427100 | 529511.6892 | 657547.0565
| Inclusion of Peak Factor 2.5 |  |  |  | 1067750 | 1323779.2231 | 1643867.6412
2. Water Demand Calculation for Commercial Buildings
▪ includes common services such as school, hospital, market, hotel, mosque, restaurant, fire service, police station etc
| occupancy type | Present member | future provision (%) | per capita consumtion (LPCD) | present water requirement (LPD) | Future water requirement (10 year) (LPD) | Future water requirement (20 year) (LPD) | Remarks
School | B1 | 400 | 2 | 45 | 18000 | 21941.8996 | 26747.0531 | Two Shift Assume, Teachers & Student =200/ shift | 375550 | 422327.0165 | 475585.14 | 0 | 0
Hospital | D1 | 250 | 1 | 450 | 112500 | 124269.9891 | 137271.3795 | Bed=150, Doctors=20, Nurse=40, Staff=40 | #REF! | #REF! | #REF! | #REF!
Hotel | A5 | 250 | 1 | 300 | 75000 | 82846.6594 | 91514.253 | Assume, Staff=50, Guests=200
Shopping Complex | F3 | 460 | 1.5 | 30 | 13800 | 16015.4634 | 18586.5991 |  | 1.3478 | 1819.596 | 909.798 | 909.798 | 18195.9604 | 121306.4024 | 2223.9507 | 1213.064 | #REF!
Grocery Store | F3 | 150 | 1.5 | 30 | 4500 | 5222.4337 | 6060.8475 |  |  | 0
Security Service | F5 | 30 | 3 | 45 | 1350 | 1814.2871 | 2438.2502 | Officer=2, Staff=28 |  | 0
Fire brigrade | F5 | 15 | 3 | 45 | 675 | 907.1436 | 1219.1251 | Officer=2, Staff=13 |  | 0
Gas Station | F4 | 10 | 1 | 45 | 450 | 497.08 | 549.0855 | Manager=1, Worker=9 |  | 0
Power Station | F5 | 15 | 1 | 45 | 675 | 745.6199 | 823.6283 | Manager=2, Staff=13 |  | 0
TNT office | F5 | 30 | 2 | 45 | 1350 | 1645.6425 | 2006.029 | Officer=4, Staff=26 |  | 0
Mosque | E3 | 1000 | 2 | 25 | 25000 | 30474.8605 | 37148.6849 | Five times per day Assume, People = 200/time |  | 0
Restaurant | A5 | 120 | 1.5 | 135 | 16200 | 18800.7614 | 21819.0511 |  |  | 0
Amphitheatre | E1 | 300 | 1 | 45 | 13500 | 14912.3987 | 16472.5655 |  |  | 0
Community Center | E1 | 1000 | 1 | 90 | 90000 | 99415.9913 | 109817.1036 |  |  | 0
Bank | F1 | 55 | 1 | 30 | 1650 | 1822.6265 | 2013.3136 | Officer=5, Staff=50 |  | 0
Temple | E3 | 60 | 1 | 15 | 900 | 994.1599 | 1098.171 |  |  | 0
|  | Total Commercial Water Demand |  |  | 375550 | 422327.0165 | 475585.14 |  |  | #REF!
|  | Inclusion of Peak Factor 3 |  |  | 1126650 | 1266981.0494 | 1426755.42 |  |  | 0
0
0
4.Water Demand for Production of Finished Goods:
Per day finished product weight (lb) | Per day finished product weight (in 1000 lb) | Code (gal/1000 lb finished goods) | future provision (%) | Peak Factor | Present water Demand (gal/day) | Present water Demand (LPD) | Future water Demand (10 year) (LPD) | Future water Demand (20 year) (LPD) |  | 1.3478 | 0
8000 | 8 | 4000 | 1 | 1.5 | 48000 | 181680 | 200687.7477 | 221684.1265
|  |  | 1.5 | 2 | 64000 | 242240 | 267583.6637 | 295578.8353
5.Water Demand Calculation for Firefighting
Assumptions
●only one fire incidence occurs per day
●each station/facility should be served by two fire hydrants at a time
●Nozzle diameter of the hydrant is 3"
●Velocity of water in the pipe is 3fps
●Each hydrant will supply water for 30 minutes
| total Volume of water flowing in one hydrant |  |  |  | = | Qxt
[5 empty] | = | π x (3/12)2/4x 3fps x 30 x 60
[5 empty] | = | 265.07 ft3
|  | total volume of water supplied by one hydrant ( ft3 ) | [5 empty] | 265.07
|  | Total number of hydrants | [5 empty] | 2
|  | total volume of water required for firefighting ( ft3) | [5 empty] | 530.14
|  | total volume of water required for firefighting ( litre) | [5 empty] | 15011.9744
Note: 1 ft3 = 28.317 litres
Note- Per Capita Water Consumption Data is taken from Table 8.6.1 , BNBC 1993.
Total Water Demand Calculation for Industrial Village
|  | Total Present Demand (LPD) | Future water requirement (10 year) (LPD) | Future water requirement (20 year) (LPD)
| Residential | 1067750 | 1323779.2231 | 1643867.6412
| Commercial | 1126650 | 1266981.0494 | 1426755.42
| Industry | 58002 | 67275.9492 | 78034.9901
| Production | 181680 | 200687.7477 | 221684.1265
| Firefighting | 15012 | 15012 | 15012
| Σ | 2449094 | 2873735.9694 | 3385354.1778

## Sheet2
Water Demand for Production of Finished Goods:
| Per day finished product weight (lb) | Per day finished product weight (in 1000 lb) | Code (gal/1000 lb finished goods) | future provision (%) | Peak Factor | Present water Demand (gal/day) | Present water Demand (LPD) | Future water Demand (10 year) (LPD) | Future water Demand (20 year) (LPD) | Future water Demand (30 year) (LPD)
| 4500 | 4.5 | 40000 | 1 | 1.5 | 282000 | 1067370 | 1179040.518 | 1302394.2429 | 1438653.4968 | Note:1 gal =3.785 litre
Water Demand for industry:
| Building description | occupancy type | Present member | future provision (%) | per capita consumtion (LPCD) | Time Factor | present water requirement (LPD) | Future water Demand (10 year) (LPD) | Future water Demand (20 year) (LPD) | Future water Demand (30 year) (LPD)
| Industrial production building | G1 | 280 | 1.03 | 40 | 1 | 11200 | 12408.5648 | 13747.5429 | 15231.0068
| emergency medical service | D2 | 12 | 0.5 | 135 | 1 | 1620 | 1702.847 | 1789.9308 | 1881.4681
| emergency fire service | F5 | 5 | 0.5 | 45 | 1 | 225 | 236.5065 | 248.6015 | 261.315
| Storage Building | H1 | 4 | 1 | 6 | 1 | 24 | 26.5109 | 29.2846 | 32.3484
| ETP | J2 | 25 | 0.2 | 8 | 1 | 200 | 204.0362 | 208.1538 | 212.3546
| Security (2 no.s) | K1 | 15 | 0.2 | 5 | 1 | 75 | 76.5136 | 78.0577 | 79.633
[6 empty] | Σ | 16276 | 17720.5341 | 19307.3666 | 21051.1854
|  | Total Industrial water demand |  |  |  |  | 1083646 | 1196761.0521 | 1321701.6095 | 1459704.6822