Determination of strainer length and position

The static water level = 180 ft
Average rate of water level declination (per year) = 2 ft
Design period= 20 years
Drawdown of 15’ while pumping each time
Safety distance = 15’
So length of the Casing pipe= (180+2*20+15+15) = 250 ft
Aquifer depth= (360-260) = 100 ft which is more than 50 ft
So 80% of the aquifer screening can be made which gives the strainer
length of = (100 * 0.80) = 80 ft
But as we know that maximum safe length of the strainer is 100’.
So, The Strainer Length = 90 ft

4 inch diameter envelop of gravel pack material will surround the
entire screen.

Length of Casing Pipe : 250 ft
Length of the Strainer : 90 ft

Selection of Strainer Size
From Gravel pack graph, D10 = 0.90 mm

To retain 90% of gravel pack material,
Slot = (D10/25.4)*1000

= (0.90/25.4)*1000

=35.43
So, we select 6 inch diameter 30 slot strainer having each opening area
of 30/1000 inch.
4 inch diameter envelop of gravel pack material will surround the entire
screen.

Strainer Size : 30 slot
4 inch Diameter Envelop of Gravel Pack Material

Yield of well:

For 30 slot strainer,
Strainer area= 15% of strainer surface area
= 0.15 x 3.1416 x Diameter x Strainer length
Here, Diameter = 6 inch, Length = 90 ft
Assume, Flow velocity = 0.10 fps
Factor of safety = 2.5
So, Yield of a well = (0.15 x 3.1416 x 6/12 x 90 x 0.1) / 2.5
                               = 0.848 ft3/s
                               = 0.848x (0.3048)3x3600x1000 lph
                               = 86508 lph

For 8 hours continuous pumping

Yield = (86508 x 8) lpd

= 692064 lpd

Zone 1 : (Residential & Commercial)

For Present,

Total water demand = (1067750+1126650+15012) lpd

= 2209412 lpd

No of wells = 2209412/692064

= 3.2 ≈ 4

For 10 years,

Total water demand = (1323779+126698+15012) lpd

= 2605772 lpd

No of wells = 2605772/692064

= 3.77 ≈ 4

For 20 years,

Total water demand = (1643868+1426755+15012) lpd

= 3085635 lpd

No of wells = 3085635/692064

= 4.5 ≈ 5

Zone 2 : (Industrial & Production)

For Present,

Total water demand = (58002+181680) lpd

= 239682 lpd

No of wells = 239682/692064

= 0.35 ≈ 1

For 10 years,

Total water demand = (67276+200688) lpd

= 267964 lpd

No of wells = 267964/692064

= 0.39 ≈ 1

For 20 years,

Total water demand = (78035+221684) lpd

= 299719 lpd

No of wells = 299719/692064

= 0.43 ≈ 1

MIT Classification of soil is presented

below:

| MIT Classification |
| --- |
| Silt/Clay | < 0.06 mm |
| Fine Sand | 0.06 – 0.20 mm |
| Medium Sand | 0.20 – 0.60 mm |
| Course Sand | 0.60 – 2.00 mm |
| Fine Gravel | > 2.00 mm |