Pump capacity:

Working Horse Power, WHP= H*Q/3960

Breaking Horse Power, BHP= WHP/ɳ

Where, ɳ= Pump Efficiency

Where, H= Total head or lift of the pump (ft)

=Static head + Velocity head + Friction head

Again, Static head = Suction head + Delivery head

So, H = hs+ hd + hv + hf

Static head:

Suction head, hs = 0 (since submersible pump)

Delivery head, hd = Static water level + Maximum building height

= 180’+60’= 240’

Velocity head:

hv = v2/ 2g  (Assuming, Velocity of water supply = 3 fps)

= 32/(2*32) =0.14’

Friction head:

For pump 1:

Friction loss is assumed to be 10% of maximum pipe length

Maximum pipe length = Maximum horizontal distance +Maximum height of the building

+ Height of overhead tank

= 642’+60’+12’ = 714’

Friction Head = Maximum pipe length* 10%

= 714’*0.1 = 71.4’

So, Total head, H = static head+ velocity head+ friction head

= 240’+ 0.14’+ 71.4’

= 311.54

Yield of well, Q = 86508 lph

= 86508/227.13

= 381 gpm

WHP= HQ/3960

= (311.54*381)/3960

= 30 HP

Let, pump efficiency, ɳ = 75%

BHP= WHP/ ɳ

= 30/0.75

= 40 HP

Similarly, pump capacity for other pumps are calculated.

| Zone | Pump Number | Phase | WHP | BHP |
| --- | --- | --- | --- | --- |
| 1 | Pump 1 | 1 & 2 | 30 | 40 |
|  | Pump 2 | 1 & 2 | 29 | 38 |
|  | Pump 3 | 1 & 2 | 28 | 37 |
|  | Pump 4 | 1 & 2 | 26 | 35 |
|  | Pump 5 | 3 | 25 | 34 |
| 2 | Pump1 | 1 , 2 & 3 | 26 | 35 |

Note : Zone 1 : Residential and Commercial area

Zone 2 : Industrial area

Phase 1 : Present water demand

Phase 2 : After 10 year water demand

Phase 3 : After 20 year water demand

Pumping schedule:

- Total water demand, water supply and net storage per hour for present, in 10 and 20 years are calculated in each zone.

- Demand curve is created for each zone

Calculations of pump schedule, water demand and demand curve are shown below: