## Sheet1
Water Distribution Network Design
Water Distribution Layout Design by Dead-end System | [8 empty] | Water Distribution Layout Design by Dead-end System
For Pump 1 : | [8 empty] | For Pump 1 :
| Present Water Demand : | [8 empty] | After 10 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch) |  |  | Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 189960 | 0.07764 | 410 | 3.7267 | 2.1783 | 3 |  |  | 1-2 | 238964 | 0.097669 | 410 | 4.6881 | 2.4432 | 3
1-3 | 132720 | 0.054245 | 335 | 2.6038 | 1.8208 | 2 |  |  | 1-3 | 163844 | 0.066966 | 335 | 3.2144 | 2.023 | 3
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments |  | Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 410 | 3 | 2.2919 | 0.99317 | 0.99317 | 59.0068 | OK | Path 1 | 1-2 | 410 | 3 | 2.2919 | 0.99317 | 0.99317 | 59.0068 | OK
Path 2 | 1-3 | 335 | 2 | 2.809 | 1.2172 | 1.2172 | 58.7828 | OK | Path 2 | 1-3 | 335 | 3 | 1.8727 | 0.81149 | 0.81149 | 59.1885 | OK
Water Distribution Layout Design by Dead-end System
For Pump 1 :
After 20 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 301692 | 0.12331 | 410 | 5.9188 | 2.7452 | 3
1-3 | 203281 | 0.083085 | 335 | 3.9881 | 2.2534 | 3
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 410 | 3 | 2.2919 | 0.99317 | 0.99317 | 59.0068 | OK
Path 2 | 1-3 | 335 | 3 | 1.8727 | 0.81149 | 0.81149 | 59.1885 | OK