## Sheet1
Water Distribution Network Design
Water Distribution Layout Design by Dead-end System | [8 empty] | Water Distribution Layout Design by Dead-end System
For Pump 2 : | [8 empty] | For Pump 2 :
| Present Water Demand : | [8 empty] | After 10 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch) |  |  | Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 171800 | 0.070218 | 266 | 3.3705 | 2.0716 | 3 |  |  | 1-2 | 196382 | 0.080265 | 266 | 3.8527 | 2.2148 | 3
1-6 | 12500 | 0.005109 | 167 | 0.24523 | 0.55878 | 2 |  |  | 1-6 | 14722 | 0.0060172 | 167 | 0.28882 | 0.60642 | 2
1-7 | 4050 | 0.0016553 | 255 | 0.079455 | 0.31807 | 2 |  |  | 1-7 | 4960 | 0.0020272 | 255 | 0.097308 | 0.35199 | 2
2-3 | 205500 | 0.083992 | 225 | 4.0316 | 2.2657 | 2 |  |  | 2-3 | 229059 | 0.093621 | 225 | 4.4938 | 2.392 | 2
2-4 | 1650 | 0.00067439 | 140 | 0.032371 | 0.20302 | 2 |  |  | 2-4 | 1823 | 0.0007451 | 140 | 0.035765 | 0.21339 | 2
2-5 | 5000 | 0.0020436 | 145 | 0.098093 | 0.35341 | 2 |  |  | 2-5 | 5000 | 0.0020436 | 145 | 0.098093 | 0.35341 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments |  | Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 266 | 3 | 1.487 | 0.64435 | 2.4975 | 57.503 | OK | Path 1 | 1-2 | 266 | 3 | 1.487 | 0.64435 | 2.4975 | 57.503 | OK
| 2-3 | 225 | 2 | 1.8866 | 0.81755 |  |  |  |  | 2-3 | 225 | 2 | 1.8866 | 0.81755
| 2-4 | 140 | 2 | 1.1739 | 0.5087 |  |  |  |  | 2-4 | 140 | 2 | 1.1739 | 0.5087
| 2-5 | 145 | 2 | 1.2158 | 0.52686 |  |  |  |  | 2-5 | 145 | 2 | 1.2158 | 0.52686
Path 2 | 1-6 | 167 | 2 | 1.4003 | 0.6068 | 1.5334 | 58.467 | OK | Path 2 | 1-6 | 167 | 2 | 1.4003 | 0.6068 | 1.5334 | 58.467 | OK
| 1-7 | 255 | 2 | 2.1382 | 0.92655 |  |  |  |  | 1-7 | 255 | 2 | 2.1382 | 0.92655
Water Distribution Layout Design by Dead-end System
For Pump 2 :
After 20 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 227815 | 0.093112 | 266 | 4.4694 | 2.3855 | 3
1-6 | 18061 | 0.0073819 | 167 | 0.35433 | 0.67168 | 2
1-7 | 6344 | 0.0025929 | 255 | 0.12446 | 0.39808 | 2
2-3 | 255533 | 0.10444 | 225 | 5.0132 | 2.5265 | 2
2-4 | 2013 | 0.00082275 | 140 | 0.039492 | 0.22424 | 2
2-5 | 5000 | 0.0020436 | 145 | 0.098093 | 0.35341 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 266 | 3 | 1.487 | 0.64435 | 2.4975 | 57.503 | OK
| 2-3 | 225 | 2 | 1.8866 | 0.81755
| 2-4 | 140 | 2 | 1.1739 | 0.5087
| 2-5 | 145 | 2 | 1.2158 | 0.52686
Path 2 | 1-6 | 167 | 2 | 1.4003 | 0.6068 | 1.5334 | 58.467 | OK
| 1-7 | 255 | 2 | 2.1382 | 0.92655