## Sheet1
Water Distribution Network Design
Distribution System Layout Design by Dead-end System | [8 empty] | Distribution System Layout Design by Dead-end System
For Pump 3 : | [8 empty] | For Pump 3 :
| Present Water Demand : | [8 empty] | After 10 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch) |  |  | Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 115000 | 0.047003 | 475.12 | 2.2561 | 1.6949 | 2 |  |  | 1-2 | 149924 | 0.061277 | 475.12 | 2.9413 | 1.9352 | 2
1-3 | 61260 | 0.025038 | 558 | 1.2018 | 1.237 | 2 |  |  | 1-3 | 71288 | 0.029137 | 558 | 1.3986 | 1.3344 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments |  | Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 475.12 | 2 | 3.9839 | 1.7264 | 1.7264 | 58.2736 | OK | Path 1 | 1-2 | 475.12 | 2 | 3.9839 | 1.7264 | 1.7264 | 58.2736 | OK
Path 2 | 1-3 | 558 | 2 | 4.6789 | 2.0275 | 2.0275 | 57.9725 | OK | Path 2 | 1-3 | 558 | 2 | 4.6789 | 2.0275 | 2.0275 | 57.9725 | OK
Distribution System Layout Design by Dead-end System
For Pump 3 :
After 20 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 173360 | 0.070856 | 475.12 | 3.4011 | 2.081 | 3
1-3 | 83501 | 0.034129 | 558 | 1.6382 | 1.4442 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 475.12 | 3 | 2.656 | 1.1509 | 1.1509 | 58.8491 | OK
Path 2 | 1-3 | 558 | 2 | 4.6789 | 2.0275 | 2.0275 | 57.9725 | OK