## Sheet1
Water Distribution Network Design
Water Distribution Layout Design by Dead-end System | [8 empty] | Water Distribution Layout Design by Dead-end System
For Pump 4 : | [8 empty] | For Pump 4 :
| Present Water Demand : | [8 empty] | After 10 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch) |  |  | Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 19000 | 0.0077657 | 194 | 0.37275 | 0.68891 | 2 |  |  | 1-2 | 19418 | 0.0079365 | 194 | 0.38095 | 0.69645 | 2
1-3 | 17500 | 0.0071526 | 239.5 | 0.34332 | 0.66116 | 2 |  |  | 1-3 | 17918 | 0.0073234 | 239.5 | 0.35153 | 0.66901 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments |  | Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 194 | 2 | 1.6267 | 0.70491 | 0.70491 | 59.295 | OK | Path 1 | 1-2 | 194 | 2 | 1.6267 | 0.70491 | 0.70491 | 59.2951 | OK
Path 2 | 1-3 | 239.5 | 2 | 2.0082 | 0.87023 | 0.87023 | 59.295 | OK | Path 2 | 1-3 | 239.5 | 2 | 2.0082 | 0.87023 | 0.87023 | 59.1298 | OK
Water Distribution Layout Design by Dead-end System
For Pump 4 :
After 20 years Water Demand :
Node | Supply (lpd) | Supply (cuft/sec) | Length (ft) | Area of Pipe req. (sq.inch.) | Dia. Of Pipe req. (inch) | Dia. Of Pipe provided (inch)
1-2 | 19881 | 0.0081258 | 194 | 0.39004 | 0.70471 | 2
1-3 | 17918 | 0.0073234 | 239.5 | 0.35153 | 0.66901 | 2
| Node | Length (ft) | Dia. Of Pipe provided (inch) | Head Loss (ft) | Head Loss (psi) | Total Head Loss (psi) | Pressure Available (psi) | Comments
Path 1 | 1-2 | 194 | 2 | 1.6267 | 0.70491 | 0.70491 | 59.2951 | OK
Path 2 | 1-3 | 239.5 | 2 | 2.0082 | 0.87023 | 0.87023 | 59.1298 | OK