Basic Design Considerations :

Hydraulic Design Equation
The Manning equation is commonly used for sewer design. Roughness co-efficient “n”in Manning’s
equation should not be less than 0.013 for new sewers made of PVC, Vitrified clay or concrete.
- Pipe sections should not be less than 5 feet long
- For new constructions assume first class construction with true and smooth inside surfaces.

Pipe Sizes
• Consider minimum pipe size 8 inches (200mm). However if wastewater volume is low pipe size at
least 6 inch is allowed.
• Smallest sewers should be larger than the building sewer connections in general use in the area
• Most common size of building connection is 6 inches but connections of 5 and 4 inches have
been used successfully in some areas

Flow Velocities
During design two critical velocities are considered –
i) Self cleansing velocity –
 It is the minimum velocity required to be attained at least once in a day to prevent solid
deposition along sewer.
 Minimum allowable velocity is 2 ft/sec (0.6 m/sec) at one-half full or full depth.
 If access for cleaning is difficult, the minimum velocity should be 3 ft/sec (1 m/sec).
ii) Non-scouring velocity
 It is the maximum limit of velocity to prevent scouring/ damage to sewer wall by solids in
wastewater.
 Its value depends on the
 Maximum allowable velocity:
- 2.5-3.0 m/sec for concrete sewer
- 3.0-3.5 m/sec for vitrified sewer
- 2.0-2.5 m/sec for brick sewer
- 3.5-4.0 m/sec for cast iron sewer

Sewer Pipe Slopes

The following table shows the minimum gravity sewer pipe slopes based on manning’s equation
with a minimum velocity of 0.6 m/s. Where practicable steeper slopes should be used.

Table: Gravity Sewer Minimum Pipe Slopes

| Size in inch (mm) | Slope m/m |
| --- | --- |
|  | n = .0.013 |
| 8 (200) | 0.0033 |
| 10 (250) | 0.0025 |
| 12 (300) | 0.0019 |
| 15 (375) | 0.0014 |
| 18 (450) | 0.0011 |
| 21 (525) | 0.0009 |
| 24 (600) | 0.0008 |
| 27 (675) | 0.0007 |
| 30 (750) | 0.0006 |
| 36 (900) | 0.0004 |

Manholes
The number of manholes must be adequately spaced so that the sewers can be easily inspected
and maintained.
Manhole Size and Spacing
Size:
• Manholes in small sewers are usually about 4 feet in diameter when the sewers have circular
cross sections
• In large sewers, larger manholes may be required to accommodate larger cleaning devices
Spacing:
• Sewers < 24 in (600mm) - Place manholes at intervals not greater than 350 ft (100m).
• Sewers 27 – 48 in (700-1200mm) - Place manholes at intervals not greater than 400 ft (120m).
• Sewers > 48 in (1200 mm) - Manholes may be placed at greater intervals depending on local
conditions like breaks in grade, location of street intersections, etc.
In addition place manholes –
• Abrupt changes in horizontal direction or slope
• Pipe size change locations

Pipe Diameter Determine

Manning’s equation,
Pipe Diameter, D (m) = 1.548 [ nQ/ √S]^0.375

Here,

Q = Cumulative Flow ( m^3/s)

n = Manning roughness coefficient (an empirical, dimensionless constant)

S = pipe slope, m/m or dimensionless

Average Wastewater Flows :

| Category | % of avg. water demand |
| --- | --- |
| Industrial | 90 |
| Residential | 75 |
| Institutional | 75 |
| Commercial | 75 |

Peak wastewater flows
Components of waste water flow include:
1. Peak flows from residential, institutional and commercial zone
2. Peak discharge of industrial waste water
3. Peak infiltration allowance (use fig-5)
Peak factors for industrial, institutional and commercial wastewater is given in table:

| Peak Factors for Different Facilities |  |
| --- | --- |
| Category | Peak Factor |
| Industrial | 2.1 |
| Institutional | 4.0 |
| Commercial | 1.8 |

Peak factor for residential wastewater :

Figure : Peaking Factor for Residential Wastewater Flows

Infiltration to Sanitary Sewer Systems
Groundwater/percolating water in the subsurface entering a sewer system through- defective pipes,
leaking pipe joints, cracked manhole walls etc.
Calculation/ estimation of infiltration for new construction can be obtained using the following
figure: