|  | Design Of Trunk Sewer |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.Calculation of Average Daily Wastewater Flow |  |  |  |  |  |  |  |
| Area Design. | Area Type | Area (sqft) | Area (ha) | Water Demand (LPD) | % of avg. water demand | Average WW Flow (LPD) | Average WW Flow (m^3/day) |
| A1 | Single Family | 54150 | 0.503 | 216000 | 75 | 162000 | 162.00 |
| A2 | Single Family | 107856 | 1.002 | 573480 | 75 | 430110 | 430.11 |
| B1 | Mix-Resid. | 28056 | 0.261 | 90224 | 75 | 67668 | 67.67 |
| B2 | Mix-Resid. | 44650 | 0.415 | 155336 | 75 | 116502 | 116.50 |
| C1 | Commercial | 26250 | 0.244 | 567450 | 75 | 425588 | 425.59 |
| C2 | Commercial | 33125 | 0.308 | 5400 | 75 | 4050 | 4.05 |
| C3 | Commercial | 34450 | 0.320 | 450000 | 75 | 337500 | 337.50 |
| C4 | Commercial | 28500 | 0.265 | 203400 | 75 | 152550 | 152.55 |
| D1 | MD's Family | 31506 | 0.293 | 10000 | 75 | 7500 | 7.50 |
| D2 | Guest House | 20826 | 0.193 | 10000 | 75 | 7500 | 7.50 |
| I1 | Idustrial | 54870 | 0.510 | 124356 | 90 | 111920 | 111.92 |
| I2 | Idustrial | 36270 | 0.337 | 117426 | 90 | 105683 | 105.68 |
| M1 | Mosque | 13300 | 0.124 | 75000 | 75 | 56250 | 56.25 |
| P1 | Park&Parking | 34770 | 0.323 | 5000 | 75 | 3750 | 3.75 |
| S1 | School&College | 27300 | 0.254 | 83400 | 75 | 62550 | 62.55 |

| 2. Calculation of Peak Daily Wastewater Flow |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Line No. | Up-stream Nodes | Down-stream Nodes | Feeder Areas | Cum. Avg. WW flow (m^3/day) | Peaking Factor | Peak WW Flow (m^3/day) |
| 1 | 1 | 2 | B1 B2 C3 C4 P1 | Res. : 176.67 Comm. : 351.98 | Res. : 3.34 Comm. : 1.8 | 1517.47 |
| 2 | 2 | 3 | A1 C1 C2 M1 | Res. : 162 Comm. : 485.89 | Res. : 3.34 Comm. : 1.8 | 1415.68 |
| 3 | 3 | 4 | A2 S1 | Res. : 430.11 Instit. : 62.55 | Res. : 3.25 Instit. : 4 | 1648.06 |
| 4 | 4 | 5 | D1 D2 I1 I2 | Res. : 15 Inds. : 217.6 | Res. : 3.34 Inds. : 2.1 | 507.06 |

*Peaking Factor for Residential Wastewater Flows graph is used to find peaking factor

| 3. Calculation of Peak Daily Flows Including infiltration |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Line No. | Feeder Areas | Total Infiltration Area (ha) | Infiltration Allowance (m^3/ha.day) | Infiltration (m^3/day) | Peak WW Flow (m^3/day) | Peak Flow (m^3/day) |
| 1 | B1 B2 C3 C4 P1 | 1.584 | 8.75 | 13.86 | 1517.47 | 1531.33 |
| 2 | A1 C1 C2 M1 | 1.179 | 8.75 | 10.32 | 1415.68 | 1426.00 |
| 3 | A2 S1 | 1.256 | 8.75 | 10.99 | 1648.06 | 1659.05 |
| 4 | D1 D2 I1 I2 | 1.333 | 8.75 | 11.66 | 507.06 | 518.72 |

*Average Infiltration rate allowance for new sewers graph is used to estimate infiltration allowance

| 4. Calculation of Cumulative Flows in Each Pipe Segment |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Line No. | Feeder Lines | In-pipe Flow (m^3/day) | Entering Flow (m^3/day) | Cumulative Flow (m^3/day) | Cumulative Flow (m^3/Sec.) |
| 1 | 0 | 0 | 1531.33 | 1531.33 | 0.0177 |
| 2 | 1 | 1531.33 | 1426.00 | 2957.33 | 0.0342 |
| 3 | 2 | 2957.33 | 1659.05 | 4616.38 | 0.0534 |
| 4 | 3 | 4616.38 | 518.72 | 5135.10 | 0.0594 |

| 5. Calculation of Pipe Diameter |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Line No. | Cumulative Flow (m^3/Sec.) | Roughness co-efficient n | Slope (m/m) | Exact Diameter (m) | Pipe Diameter (mm) | Full Flow (m^3/day) |
| 1 | 0.0177 | 0.013 | 0.0033 | 0.195 | 200 | 1629 |
| 2 | 0.0342 | 0.013 | 0.0033 | 0.250 | 300 | 4802 |
| 3 | 0.0534 | 0.013 | 0.0033 | 0.296 | 300 | 4802 |
| 4 | 0.0594 | 0.013 | 0.0033 | 0.308 | 375 | 8707 |

| 6. Check With V |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Line No. | Q (m^3/day) | Qfull (m^3/day) | Q/Qfull | d/D | V/Vfull | Vfull (ft/sec) | V (ft/esc) | Comments |
| 1 | 1531 | 1629 | 0.94 | 0.86 | 1.04 | 2.0 | 2.05 | OK |
| 2 | 2957 | 4802 | 0.62 | 0.64 | 0.9 | 2.6 | 2.32 | OK |
| 3 | 4616 | 4802 | 0.96 | 0.88 | 1.05 | 2.6 | 2.71 | OK |
| 4 | 5135 | 8707 | 0.59 | 0.63 | 0.89 | 3.0 | 2.66 | OK |

*d/D , V/Vfull  is determined from Hydraulic elements for circular sewers graph