## Sheet1
DESIGN OF WATER SUPPLY AND DRAINAGE NETWORK OF A 09 STOREY BUILDING
A. Calculation of water demand of a typical 09 storey building
On each typical apartment, the fixture unit load is
2 bathroom, (private, with flush tank for closet) |  |  |  | 2 x 6 FU
1 kitchen with 1 sink (FU = 2) and 1 tap (FU = 1) |  |  |  | 1x2 + 1x1
1 basin in the dining room area |  |  |  | 1x1
|  |  | ∑ | 16 FU
since 09 storey building and groundfloor reserved as garage,
16FU x 16 apartments = 256 FU
Car wash tap |  | 1 FU
1 toilet for guards |  | 6 FU
| ∑ | 263 FU
NB: Values for fixture unit has been taken from table P1: Water supply Fixture Unit (wsfu) values for various plumbing fixtures
From curve 1 (Since flush tanks used) in Fig.- P1: Water Supply Demand For Various Load in Water Supply Fixture Units (Wsfu)
demand = 82 gpm
assuming 6 person per flat
6*16 flats * 36 gal per person per day = 3456 gal per day required
B. Dimension of Underground water reservoir
water is stored in underground water reservoir with one day reserve
assuming storage required of 3456*2 gal = 1108 cft (6.24 gal = 1 cft)
if reservoir placed under the staircase area, a 20' x 10' area selected
height of reservoir required = 1108 cft / 200 ft2 = 5.5' (6" extra provided)
using a thumb rule of 10:1, 09 storey building will require 09' foundation thus 9' depth of U/G reservoir can be provided
Dimension of U/G water reservoir = 20' x 10' x 9'
C. Dimension of Overhead water reservoir
if 1 hr pumping twice daily = 3456 gal/ 2 = 1728 gal/hr
Volume of O/H tank = 1728 gal + provision for firefighting water
( atleast 30 min supply at 175 - 250gpm)
assuming 200 gpm required for firefighting water provision,
volume required = 200 gpm * 30 min = 6000 gal
total volume of water required = 1728 + 6000 = 7728 gal = 1239 ft^3
if 18'x9' area provided, depth = 1239/162 = 7.65'
a Free- board of 12'' is provided (range from 6" to 12")
Dimension of Overhead water reservoir is 18' x 9' x 8.5' and is at a height of 7.5'

## Sheet3
D. Design of Riser Pipe and Pump
water carried at 1728 gal/hr = 29 gal/min
assuming velocity withing 8-10 ft/sec ( velocity 8 fps is taken)
from fig. - P4 a 1.25" diameter riser is provided, and the corresponding head loss is 8 psi/100'
E. Calculation of pump capacity
Total length of riser (L) = total building height (10 ft per floor) + 9’ from UGWR + OH tank inlet height above top roof surface.
Total length of riser (L) = 10'*9 + 9' + 18' = 117'
Total Frictional head HL = (hL * L)/100 + 8 psi required pressure at the O/H tank + 5 psi minor loss due to bend
Total Frictional head HL = 8/100*117 + 8 + 5 = 22.36 psi
Frictional head in ft Lh = HL *144 /62.2 = 22.36*144/62.2 = 51.77'
Velocity Head = v^2/2g = 10^2/(2*32) = 1.56'
Total Head, H = Static head (L) + Velocity head + Friction head (Lh)
Total Head, H = 117' + 1.56' + 51.77' = 170.33'
if efficiency of the pump is 65% (60- 65% efficiency acceptable range)
required HP of the pump = HQ/(3960 E) = 170.33' * 29 gpm / (3960 * 0.65) = 1.92 HP
provide a pump of 2 HP
[13 empty] | psi | kpa
[12 empty] | 6 | 6.95 | 47.9202 | 9.144 | 41.691 | 6.0465
[12 empty] | 6 | 7.95 | 54.8152 | 12.192 | 64.6664 | 9.3787
[12 empty] | 7 | 9.275 | 63.9511 | 15.24 | 85.4009 | 12.3859
[12 empty] | 7 | 10.275 | 70.8461 | 18.288 | 108.3763 | 15.7181
[12 empty] | 8 | 11.6 | 79.982 | 21.336 | 129.1108 | 18.7253
[12 empty] | 11 | 13.575 | 93.5996 | 24.384 | 145.3636 | 21.0825
[12 empty] | 15 | 15.875 | 109.4581 | 27.432 | 159.3755 | 23.1146
0
0
0
[12 empty] | 13 | 20.225 | 139.4514 | 30.48 | 159.2526 | 23.0968
[12 empty] | 15 | 22.275 | 153.5861 | 33.528 | 174.9883 | 25.379
Design of Downfeed zone pipes
required faucet pressure at top floor = 5psi
assuming 2 psi pressure loss for different fittings
two downfeed zones are selected, 1 downfeed pipe is 1 inch with friction loss 10 psi/100' supplying water to flats upto 3rd floor
and the other pipe is 3/4 inch with friction loss 14 psi/100' upto ground floor
Floor | FU | Accumulated FU | Demand flow (gpm) | Length of pipe (ft) | pipe size (in) | pressure loss (psi) | pressure loss (kPa) | Length of pipe (m) | Available pressure (kpa) | Available pressure (psi) | Comment
9 | 16 | 112 | 45 | 30 | 1.5 | 6.95 | 47.9202 | 9.144 | 41.691 | 6.0465 | ok
8 | 16 | 96 | 42.5 | 40 | 1.5 | 7.95 | 54.8152 | 12.192 | 64.6664 | 9.3787 | ok
7 | 16 | 80 | 39 | 50 | 1.5 | 9.275 | 63.9511 | 15.24 | 85.4009 | 12.3859 | ok
6 | 16 | 64 | 35 | 60 | 1.25 | 10.275 | 70.8461 | 18.288 | 108.3763 | 15.7181 | ok
5 | 16 | 48 | 30 | 70 | 1.25 | 11.6 | 79.982 | 21.336 | 129.1108 | 18.7253 | ok
4 | 16 | 32 | 20 | 80 | 1 | 13.575 | 93.5996 | 24.384 | 145.3636 | 21.0825 | ok
3 | 16 | 16 | 8 | 90 | 3/4 | 15.875 | 109.4581 | 27.432 | 159.3755 | 23.1146 | ok
Floor | FU | Accumulated FU | Demand flow (gpm) | Length of pipe (ft) | pipe size (in) | pressure loss (psi) | pressure loss (kPa) | Length of pipe (m) | Available pressure (kpa) | Available pressure (psi) | Comment
2 | 16 | 23 | 15 | 100 | 3/4 | 20.225 | 139.4514 | 30.48 | 159.2526 | 23.0968 | ok
1 | 7 | 7 | 5 | 110 | 3/5 | 22.275 | 153.5861 | 33.528 | 174.9883 | 25.379 | ok
Demand Flow is found from curve 2 in Fig.- P1: Water Supply Demand For Various Load in Water Supply Fixture Units (Wsfu)
Pressure loss is found from fig - P4
Minimum Pressure Requirement
at the top of the shower (which is approximately 3' from the ceiling) water pressure is 18' *62.2/144 = 7.78 psi thus head loss cannot exceed 2.1psi to provide a 5.78 psi at the shower faucet. As shown above, the pressure loss is within this limit
Maximum Pressure Requirement
the static head gained at the bottom of the downfeed zone is (15'from Overhead tank + 87' to the bottom most faucet at Ground floor) = 102' * 0.432 = 44.01 psi and this has to balance the pressure loss in the pipes. Since this head gain is below 50 psi, there is no need for a pressure reducing valve at any junction