## Slide 1
Centrifugal Pumps Course Co-ordinator Dr. Anupam Chowdhury Associate Professor Department of Civil Engineering, RUET

## Slide 2: Centrifugal Pumps
Demour’s centrifugal pump - 1730
Theory
  conservation of angular momentum
  conversion of kinetic energy to potential energy
Pump components
  rotating element - impeller
  encloses the rotating element and seals the pressurized liquid inside – casing or housing

## Slide 3: Centrifugal Pumps
Impeller
Vanes
Casing
Suction Eye
Impeller
Discharge
Flow Expansion
Broad range of applicable for flows and heads
Higher heads can be achieved by increasing the diameter or the rotational speed of the impeller

## Slide 4: Centrifugal Pump
Centrifugal pumps (radial-flow pumps) are the most used pumps for hydraulic purposes. For this reason, their hydraulics will be studied in the following sections.

## Slide 7: Main Parts of Centrifugal Pumps
which is the rotating part of the centrifugal pump.
It consists of a series of backwards curved vanes (blades).
The impeller is driven by a shaft which is connected to the shaft of an electric motor.
Impeller:

## Slide 8: Main Parts of Centrifugal Pumps
Which is an air-tight passage surrounding the impeller
designed to direct the liquid to the impeller and lead it away
Volute casing: It is of spiral type in which the area of the flow increases gradually.
Casing

## Slide 9
Suction Pipe.
Delivery Pipe.
The Shaft: which is the bar by which the power is transmitted from the motor drive to the impeller.
The driving motor: which is responsible for rotating the shaft. It can be mounted directly on the pump, above it, or adjacent to it.

## Slide 10
Note that a centrifugal pump can be either submersible (wet) or dry.

## Slide 12: Pump Efficiency
or
Which is the power input delivered from the motor to the impeller of the pump.

## Slide 13
Motor efficiency :
which is the power input delivered to the motor.
Overall efficiency of the motor-pump system:

## Slide 14: Cavitation of Pumps and NPSH
In general, cavitation occurs when the liquid pressure at a given location is reduced to the vapor pressure of the liquid.
For a piping system that includes a pump, cavitation occurs when the absolute pressure at the inlet falls below the vapor pressure of the water.
This phenomenon may occur at the inlet to a pump and on the impeller blades, particularly if the pump is mounted above the level in the suction reservoir.

## Slide 15
Under this condition, vapor bubbles form (water starts to boil) at the impeller inlet and when these bubbles are carried into a zone of higher pressure, they collapse abruptly and hit the vanes of the impeller (near the tips of the impeller vanes). causing:
Damage to the pump (pump impeller)
Violet vibrations (and noise).
Reduce pump capacity.
Reduce pump efficiency

## Slide 16: How we can avoid Cavitation ??
To avoid cavitation, the pressure head at the inlet should not fall below a certain minimum which is influenced by the further reduction in pressure within the pump impeller.
To accomplish this, we use the difference between the total head at the inlet , and the water vapor pressure head

## Slide 17
Where we take the datum through the centerline of the pump impeller inlet (eye). This difference is called the Net Positive Suction Head (NPSH), so that
There are two values of NPSH of interest. The first is the required NPSH, denoted (NPSH)R , that must be maintained or exceeded so that cavitation will not occur and usually determined experimentally and provided by the manufacturer.
The second value for NPSH of concern is the available NPSH, denoted (NPSH)A , which represents the head that actually occurs for the particular piping system. This value can be determined experimentally, or calculated if the system parameters are known.

## Slide 18: How we can avoid Cavitation ??
For proper pump operation (no cavitation) :
(NPSH)A > (NPSH)R

## Slide 19: Determination of (NPSH)A
datum
hs
applying the energy equation between point (1) and (2), datum at pump center line

## Slide 20
Note that (+) is used if hs is above the pump centerline (datum).

## Slide 21: Thoma’s cavitation constant
The cavitation constant: is the ratio of (NPSH)R to the total dynamic head (Ht) is known as the Thoma’s cavitation constant ( )
Note: If the cavitation constant is given, we can find the maximum allowable elevation of the pump inlet (eye) above the surface of the supply (suction) reservoir.

## Slide 22: Example 1
A Pump has a cavitation constant = 0.12, this pump was instructed on well using UPVC pipe of 10m length and 200mm diameter, there are elbow (ke=1) and valve (ke=4.5) in the system. the flow is 35m3 and The total Dynamic Head Ht = 25m (from pump curve) f=0.0167
Calculate the maximum suction head

## Slide 24: Selection of A Pump
It has been seen that the efficiency of a pump depends on the discharge, head, and power requirement of the pump. The approximate ranges of application of each type of pump are indicated in the following Figure.

## Slide 25: Selection of A Pump
In selecting a particular pump for a given system:
The design conditions are specified and a pump is selected for the range of applications.
A system characteristic curve (H-Q) is then prepared.
The H-Q curve is then matched to the pump characteristics chart which is provided by the manufacturer.
The matching point (operating point) indicates the actual working conditions.

## Slide 26: System Characteristic Curve
The total head, Ht , that the pump delivers includes the elevation head and the head losses incurred in the system. The friction loss and other minor losses in the pipeline depend on the velocity of the water in the pipe, and hence the total head loss can be related to the discharge rate.
For a given pipeline system (including a pump or a group of pumps), a unique system head-capacity (H-Q) curve can be plotted. This curve is usually referred to as a system characteristic curve or simply system curve. It is a graphic representation of the system head and is developed by plotting the total head, over a range of flow rates starting from zero to the maximum expected value of Q.

## Slide 28
System Characteristic Curve

## Slide 29: Pump Characteristic Curves
Pump manufacturers provide information on the performance of their pumps in the form of curves, commonly called pump characteristic curves (or simply pump curves).
In pump curves the following information may be given:
    the discharge on the x-axis,
    the head on the left y-axis,
    the pump power input on the right y-axis,
    the pump efficiency as a percentage,
    the speed of the pump (rpm = revolutions/min).
    the NPSH of the pump.

## Slide 31
Pumps Group

## Slide 34
The pump characteristic curves are very important to help select the required pump for the specified conditions.
If the system curve is plotted on the pump curves in we may produce the following Figure:
The point of intersection is called the operating point.
This matching point indicates the actual working conditions, and therefore the proper pump that satisfy all required performance characteristic is selected.
Matching the system and pump curves.

## Slide 36: Example 2
For the following pump, determine the required pipes diameter to pump 60 L/s and also calculate the needed power.
Minor losses 10 v2/2g
Pipe length 10 km
roughness = 0.15 mm
Hs = 20 m
0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | Q L/s
45 | 44.7 | 43.7 | 42.5 | 40.6 | 38 | 35 | 31 | Ht
- | 35 | 50 | 57 | 60 | 60 | 53 | 40 | 

## Slide 37
To get 60 L/s from the pump Hs + hL must be < 35 m
Assume the diameter = 300mm
Then:

## Slide 39
Assume the diameter = 350mm
Then:

## Slide 40: Multiple-Pump Operation
To install a pumping station that can be effectively operated over a large range of fluctuations in both discharge and pressure head, it may be advantageous to install several identical pumps at the station.
Pumps in Parallel
Pumps in Series

## Slide 41: (a) Parallel Operation
Pumping stations frequently contain several (two or more) pumps in a parallel arrangement.
Q1
Q2
Q3
Pump
Pump
Pump
Manifold
Qtotal
Qtotal =Q1+Q2+Q3

## Slide 42
In this configuration any number of the pumps can be operated simultaneously.
The objective being to deliver a range of discharges, i.e.; the discharge is increased but the pressure head remains the same as with a single pump.
This is a common feature of sewage pumping stations where the inflow rate varies during the day.
By automatic switching according to the level in the suction reservoir any number of the pumps can be brought into operation.

## Slide 43: How to draw the pump curve for pumps in parallel???
The manufacturer gives the pump curve for a single pump operation only.
If two or more pumps are in operation, the pumps curve should be calculated and drawn using the single pump curve.
For pumps in parallel, the curve of two pumps, for example, is produced by adding the discharges of the two pumps at the same head (assuming identical pumps).

## Slide 44: Pumps in series & Parallel
Pumps in Parallel:

## Slide 46: (b) Series Operation
The series configuration which is used whenever we need to increase the pressure head and keep the discharge approximately the same as that of a single pump
This configuration is the basis of multistage pumps; the discharge from the first pump (or stage) is delivered to the inlet of the second pump, and so on.
The same discharge passes through each pump receiving a pressure boost in doing so

## Slide 47
Q
Pump
Pump
Pump
Q
Htotal =H1+H2+H3

## Slide 48: How to draw the pump curve for pumps in series???
the manufacturer gives the pump curve for a single pump operation only.
For pumps in series, the curve of two pumps, for example, is produced by adding the heads of the two pumps at the same discharge.
Note that, of course, all pumps in a series system must be operating simultaneously

## Slide 49
H
Q
Q1
H1
H1
H1
2H1
H1
3H1
Single pump
Two pumps in series
Three pumps in series

## Slide 50: Similarity Laws: Affinity laws
The actual performance characteristics curves of pumps have to be determined by experimental testing.
Furthermore, pumps belonging to the same family, i.e.; being of the same design but manufactured in different sizes and, thus, constituting a series of geometrically similar machines, may also run at different speeds within practical limits.
Each size and speed combination will produce a unique characteristics curve, so that for one family of pumps the number of characteristics curves needed to be determined is impossibly large.

## Slide 51
The problem is solved by the application of dimensional analysis and by replacing the variables by dimensionless groups so obtained. These dimensionless groups provide the similarity (affinity) laws governing the relationships between the variables within one family of geometrically similar pumps.
Thus, the similarity laws enable us to obtain a set of characteristic curves for a pump from the known test data of a geometrically similar pump.

## Slide 52: Change in pump speed (constant size)
If a pump delivers a discharge Q1 at a head H1 when running at speed N1, the corresponding values when the same pump is running at speed N2 are given by the similarity (affinity) laws:
where Q = discharge (m3/s, or l/s).
H = pump head (m).
N = pump rotational speed (rpm).
Pi = power input (HP, or kw).

## Slide 53
Therefore, if the pump curve for speed N1 is given, we can construct the pump curve for the speed N2 using previous relationships.
Effect of speed change on pump characteristic curves.
N1
N2

## Slide 54: (b) Change in pump size (constant speed)
A change in pump size and therefore, impeller diameter (D), results in a new set of characteristic curves using the following similarity (affinity) laws:
where D = impeller diameter (m, cm).
Note : D indicated the size of the pump

## Slide 55: Example 3

## Slide 56
Solution

## Slide 58: Specific Speed
Pump types may be more explicitly defined by the parameter called specific speed (Ns) expressed by:
Where: Q = discharge (m3/s, or l/s).
H = pump total head (m).
N = rotational speed (rpm).

## Slide 59
This expression is derived from dynamical similarity considerations and may be interpreted as the speed in rev/min at which a geometrically scaled model would have to operate to deliver unit discharge (1 l/s) when generating unit head (1 m).
The given table shows the range of Ns values for the turbo-hydraulic pumps:
Pump type | Ns range (Q - l/s, H-m)
centrifugal | up to 2600
mixed flow | 2600 to 5000
axial flow | 5000 to 10 000

## Slide 60: Example 4
A centrifugal pump running at 1000 rpm under current operating condition. The pump and system curve are given in the figure. Estimate the speed to reduce the flow to one-half.
Discharge (m3/min) | 0 | 4.5 | 9.0 | 13.5 | 18.0 | 22.5
Head available (m) | 22.5 | 22.2 | 21.6 | 19.5 | 14.1 | 0
Head required (m) | 15.0 | 15.4 | 16.6 | 18.6 | 21.4 | 25.0

## Slide 62
From the previous Figure, The operating point is:
    QA = 14 m3/min
    HA = 19 m
At reduced speed: For half flow (Q = 7 m3/min) there will be a new operating point B at which:
    QB = 7 m3/min
    HB = 16 m
How to estimate the new speed ?????

## Slide 63
A
B

## Slide 64
This curve intersects the original curve for N1 = 1000 rpm at C where Qc= 8.2 m3/ hr and Hc= 21.9 m, then
N2 = 855rpm

## Slide 65
A
B
C

## Slide 66: Example 5
A pump was designed to satisfy the following system
9 | 6 | 3 | Q (m3/hr)
38 | 20 | 12 | hf (m)
Pipe diameter is 50mm
Check whether the pump is suitable or not

## Slide 68
1- Draw the system curve and check the operation point

## Slide 69
There are an operation point at:
Q = 9 m3/hr
H =58m
NPSHR =4.1
Then Check NPSHA
pump is not suitable, the cavitation will occur

## Slide 70: Example 6
Abbreviations:
G.V = Gate Valve
C.V = Check Valve
A.V = Air release Valve
E.R = Eccentric Reducer
C.I = Concentric increase
I.N = Inlet Nozzle
O.N = Outlet Nozzle
S.P = Suction Pipe
D.P = Delivery Pipe
W.W = Wet Well
D.W = Dry Well

## Slide 71: Data:
Flow rates and dimensions:
Qmax = 0.05 m3/s Qmin = 0.025 m3/s
LS.P = 5.0 m LD.P = 513.5 m
DS.P = 250mm DD.P = 200mm
Hstat = 5.3 m, hS = 3.0 m
Minor Losses Coefficients (k):
G.V = 0.1 C.V = 2.5 A.V = 0.05,
E.R = 0.1 C.I = 0.05 Elbow = 0.2
Bends in D.P = 0.05,
Entrance of S.P = 0.3 (bell mouth)
Coefficient of friction:
f = 0.02 (assumed constant).

## Slide 72
Pump characteristic curves:

## Slide 73: Required??
The given Figure shows a pump station.
Use the pump characteristic curves and the data given above to:
Choose a suitable pump which satisfies the requirements of the piping system shown,
Find the power and efficiency of the pump,
Find the overall efficiency (motor and pump) if the motor efficiency is given to be 90%, also find the required power input to the motor.
Check the pump for cavitation at T = 25oC

## Slide 74: Solution
A. Pump Selection:
The first step in selecting a pump is to draw the system curve:
To draw the system curve we need to calculate the values of Ht that correspond to several values of Q, using :
We start with Qmax = 0.05 m3/s as the first value of Q in the system and find the corresponding Ht
or

## Slide 75
Head losses in the suction pipe:
For Qmax = 0.05 m3/s.
Friction losses:
Minor losses:

## Slide 76
Head losses in the delivery pipe:
For Qmax = 0.05 m3/s.
Friction losses:
Minor losses:

## Slide 77: Therefore
therefore, we found the first point on the system curve:
(Q, H) = (0.05, 12.6)
which is the operating point of the system at Qmax.
Similarly, we need to determine at least three points (Q, H) to draw the system curve.

## Slide 78
System curve

## Slide 79
Operating point
System curve
12.6
It is clear from the above figure that the required pump is the
35-cm impeller pump

## Slide 80: Pump Power Input and Efficiency
From the pump curve we can read Pi = 7.5 kw
and hence

## Slide 81: Overall Efficiency and Motor Power Input
Overall efficiency
and hence

## Slide 82: Check for Cavitation:
To prevent cavitation we must have:
(NPSH)A (NPSH)R
From pump curve figure we can read:
  (NPSH)R = 3 m at Qmax = 0.05 m3/s.
For water at T=25oC, Patm= 101 kN/m2, and Pvapor = 3.17 kN/m2.
Using the equation
we can write
no cavitation.

## Slide 83: Home Work