## Slide 1
Course Title: Environmental Engineering – I
Course Code: CE 3141
Credit hour: 3.0,
Contact hour: 3 hr/Week,
Class Test: 4 nos.

## Slide 2: Environmental Engineering-1
Syllabus:
Introduction to environmental engineering, community and environment, clean water, sanitation and health, introduction to water supply, population and water requirement.
Water supply sources, groundwater and surface water, common water supply system with specific reference to Bangladesh, different types of hand pumps, problem of water supply, presence of iron and arsenic, hardness salinity. Alternative technologies for problem areas in Bangladesh: Shallow Shrouded Tube well (SST), Very Shallow Shrouded Tube well (VSST), pond sand Filter (PSF), Deep-set technologies.
Water collection and transportation, head works, pumps and pumping machinery, water distribution system, analysis and design of distribution network, fire hydrants, leak detection, unaccounted for water, alternative technologies, solar stills, rain water harvesting.
Water quality and treatment, water quality parameters and standards, water treatment: plain sedimentation, flocculation and settlement, filtration, other treatment methods, small scale iron and arsenic removal units, other low-cost treatment methods for rural communities, monitoring and sanitary protection of water supply distribution system.
Socio-economic aspects of WSS, Socio-economy of rural and urban Bangladesh. Demographic characteristics, power structure, cultural issues (traits), rural leadership, local government structure, influence of socio-economic aspects on community water supply and sanitation, concept of community participation, participatory planning, community organization, community mobilization, sustainable development approach, gender issues conceptual frame, women empowerment, gender auditing, gender balance and sensitivity.

## Slide 3: Environmental Engineering-1
Reference Books:
Environmental Engineering – H.S. Peavy, D.R. Rowe & G. Tchobanoglous
Environmental Engineering – Davis & Cornwell
Water Supply & Sanitation – Ahmed & Rahman
Water Supply Engineering – M.A. Aziz
Water Supply and Sanitation Engineering – Rangwala
Small Community Water Supply – Technical Paper Series, IRC
Water Supply and Sewerage – E.W. Steel & T.J. McGhee
Low Cost Water Supply and Waste Management – Training for trainers course by ITN

## Slide 4: Environmental Engineering-1
Learning Outcome:
The students will learn the following topics through the successful completion of this part:
Water collection and transportation, Fire hydrants and Head works
Pumps and pumping machineries in water supply
Analysis and design of distribution network
Leak detection, unaccounted for water, solar stills, rainwater harvesting
Water quality standard and treatment
Small scale water treatment units
Socio-economic aspects in water supply system
Gender aspects in urban and rural water supply
Water safety plan

## Slide 5: Environmental Engineering-1
CE3141
Lecture -1
Week-1, Sunday
27-12-2020

## Slide 6: Water Collection and Transportation
Collection of water is the drawing of water from the sources of water, commonly known as intakes.
The collection system is a set of engineering works designed to convey water from a source to a distribution system via treatment plant and includes intakes, suction pipes, delivery pipes and pumping stations.
Transportation of water is the conveyance of water from the intake to the treatment plant and also to the distribution systems.

## Slide 7: What is Intake?
The intake is a device placed in a surface water source to permit the withdrawal of water from the source and then discharge it into intake pipe through which it will flow into the water-works system.
It consist of the opening, strainer, or grating through which the water enters, and the conduit conveying the water, usually by gravity, to a well or sump.
From the well the water is pumped to the mains or treatment plant.
Intakes should be so located and designed that possibility of interference with the supply is minimized and where uncertainty of continuous serviceability exists, intakes should be duplicated.

## Slide 8: Considerations for Designing and Locating Intake
The following must be considered in designing and locating intakes:
The source of supply, whether impounding reservoir, lake, or river (including the possibility of wide fluctuation in water level);
The character of the intake surroundings, depth of water, character of bottom, navigation requirements, the effects of currents, floods and storms upon the structure and in scouring the bottom;
The location with respect to sources of pollution; and
The prevalence of floating material such as ice, logs, and vegetation.

## Slide 9: Intake Velocity and Depth
Intake entrance should lie 3 to 5 m below the water surface but 1 to 2 m above the river, lake or reservoir floor to keep bottom sediments out of intakes.
The entrance velocities are kept down to 7.6 to 10 m/sec. At such low velocities, vegetation, debris and other materials are not entrained in the flowing water, fish and other aquatic lives are well able to escape from the intake current.
Gratings or screens of 1 to 3 meshes to a centimeter are provided at the intake entrance.

## Slide 10: Intake Pipe
Intakes are connected to the banks of rivers or to the shores of lakes and reservoirs (i) by pipelines (often laid with flexible joints) or (ii) by tunnels blasted through rock beneath the floor.
The pipelines are generally laid in a trench on the riverbank or on the lake or reservoir floor and covered after completion.
Pipe passing through the foundation of dam are subjected to heavy loads and to stresses caused by consolidation of the foundation.
Intake pipes are designed to operate at self-cleansing velocities, 14 to 19 cm/sec.
Flow may be by gravity or by suction.

## Slide 11: Pumping Station
Pump wells are generally located on shore or banks.
Suction lift including friction should not exceed 5 to 6 m accordingly.
Pump wells are often quit deep.
The determining factor is the elevation of water level in the river, lake or reservoir in times of drought.

## Slide 12: Design Considerations
Following are the important considerations for design of an intake:
Selection of a particular type for the given source.
The magnitude of the external forces (waves, currents and blows from floating and submerged objects) to be resisted by the intake.
Consideration of the total lift from the source to the treatment plant and selection of a suitable pumping unit.
Determination of the total length of suction and delivery mains, head losses due to friction and small bends, enlargement and reduction.

## Slide 13: Design Considerations
Selection of a suitable screen to provide around the intake pipe not to permit entry of large and small objects, such as logs, stones, aquatic lives and vegetation.
Installation of intake valves or porthole at 2 or 3 different levels to get the best available quantity of water, eliminating seasonal fluctuation of waster levels.
Determination of cost-benefit ratio. To reduce the cost, the intake elevation is often made higher so that the water flows to the treatment plant by gravity.
Assurance of the safety of the intake structure, provision of future extension and installation of standby unit of pumps.

## Slide 14: Environmental Engineering-1
CE 3141
Lecture -2
Week-2, Sunday
19-02-2022

## Slide 15: Types of Intakes
The intakes are mainly of the following four types:
Canal intakes
Reservoir or lake intakes
River intakes and
Portable intakes.

## Slide 16: Canal Intakes
An intake chamber is constructed in the canal section. This results in the reduction of waterway which increases the velocity of flow. It therefore becomes necessary to provide pitching on the downstream and upstream portions of canal near intake.
The entry of water in the intake chamber takes through the coarse screen and the top of outlet pipe is provided with fine screen. The inlet to outlet pipe is of bell-mouth shape with perforations of fine screen on its surface.
The outlet valve is operated from the top and it controls the entry of water into the outlet pipe from where it is taken to the treatment plant.

## Slide 17: Canal Intakes
As the water level in the canal section practically remains constant, it is not necessary to provide intake pipe at various levels. To reach up to the bottom of intake, the steps should be provided in zigzag manner starting from manhole.
The flow velocity through the outlet pipe is usually kept as about 1.50 m/sec and it helps in determining the area and diameter of the withdrawal conduit.
For designing the area of coarse screen, the flow velocity is limited to as low as about 150 mm/sec or so. The flow velocity through the bell-mouth shaped inlet is limited to about 300 mm/sec or so.

## Slide 18: Lake and Reservoir Intake
Lake intakes are sited with due reference to sources of pollution, prevailing winds and surface currents.
Reservoir intakes resemble lake intakes but generally lie closer to bank in the deepest part of the reservoir. They are often incorporated into the impounding structure itself.

## Slide 19: Portable Intakes
In case of emergencies such as festival sites, wars, etc., it sometimes becomes necessary to draw water with the help of a movable intake.
It essentially consists of a truck fitted with a pumping plant. The truck is brought to the site and it is placed in such a position that it becomes possible to immerse the suction pipe of the pump. The end of the suction pipe is kept just above the bed level of water source and it is also provided with screen or strainer.
Thus the water lifted by the portable intake is relatively free from suspended solids. The water is then conveyed through the discharge pipe of the pumping plant.

## Slide 20: River Intake
Understandably, river intakes are constructed well upstream from points of discharge of sewage and industrial wastes.
Optional location will take advantages of deep water, a stable bottom, and favorable water quality, all with proper reference to protection against floods, debris and river traffic.
Where the river bed shifts or depth of flow varies greatly, intake pumps may be mounted on carriage that are moved up and down on the river bank to stay within desired suction lift as flows rise and fall.

## Slide 21: River Intake
Control Room
Central impervious core
F.S.L
Screen
Upstream rack to remove debris
L.W.L
Gate
Earthen Dam
Intake well
Outlet pipe
Figure: Intake well for earthen dam

## Slide 22: Transportation of Water
The arrangement for the transportation of water from the source of supply to the treatment plants and subsequent distribution to the consumers form an important part of the water-works system.
The source of supply usually being at some distance away from towns and cities, it is necessary to construct structures for the transportation of water.
These structures are known as pipes and conduits.
There are two general classes of pipes; (i) Pressure pipes in which the water flows under hydraulic pressure, and (ii) Gravity pipes (open channels) in which the water flows in gravity.

## Slide 23: Transportation of Water
A pressure pipe is also defined as a pipe flowing full.
Such pipes are often less costly than open channels (canals and flumes) because they can generally follow a shorter route.
If water is scare, pressure pipes may be used to avoid loss of water by seepage and evaporation, which generally occurs in open channels.
Pressure pipes are preferable for public water supplies because of the reduced opportunity for pollution.
The open channel may take the form of canal, flume, tunnel, aqueduct or partly filled pipe.
Open channels are characterized by a free water surface, in contrast to pressure pipes, which always flow full.

## Slide 24: Desirable Qualities of Pressure Pipes
The desirable qualities of pressure pipes are as follows:
They should be made of durable materials so that no leakage develops causing wastage of water.
They should be strong and of sufficient thickness to withstand both internal and external stresses.
The inner surface of the pipe should be very smooth so that the resistance to flow is minimum.
The pipe materials should not impart any physical and chemical effects to water.

## Slide 25: Desirable Qualities of Pressure Pipes
The desirable qualities of pressure pipes are as follows:
The pipes should be light so that transporting, handling and laying the pipe under different conditions of topography, geology and communication become easier.
Low initial cost and maximum service period of pipes are desirable.
The pipe materials should be so selected that annual maintenance cost is low, joints can be made easily, offer adequate resistance to the corrosive characteristics of soil and water and highly skilled labour is not required for their laying and construction.
The pipe sections should possess good hydraulic properties.

## Slide 26: Corrosion of Metal Pipe
Generally pipes are made by various materials like steel, cast iron, concrete, asbestos cement, vitrified-clay, PVC, GI, copper, wrought iron, plastic, asphaltic fiber and lead. But metal pipes are subject to corrosion.
Corrosion is a phenomenon by which metals and their alloys are attacked by the environment consisting of chemicals.
There are mainly two types of corrosion in pressure water pipes, (i) External corrosion and (ii) Internal corrosion.
The external agents like biological action, oxygen, etc. cause external corrosion, and the internal corrosion is generally attributed primarily to the nature of water, which flows through pipes.

## Slide 27: Corrosion of Metal Pipe
The chemical attacks of an environment upon a result in the oxidation of the metals and the formation of corrosive products, usually the oxides, hydroxides, carbonates, sulphides, etc.
In most cases, corrosion product is insoluble in the environment and forms a separate phase on or adjacent to the metal.
Hence, corrosion may be defined simply as the process by which the metals and their alloys are destroyed by chemical or electrochemical means.

## Slide 28: Causes of Corrosion of Metal Pressure Pipes
Following are the important causes of corrosion of metal pressure pipes:
Pitting: Localized pitting is usually caused in metal pipes by the concentration of electric currents resulting from the potential differences on the metal surface, which accelerates. This process is also accelerated by dissolved oxygen content of flowing water.
Influence of acids and alkalies: Acidity and alkalinity of water passing through pipes will help vigorously to corrode pipes.
Influence of sulphurous compounds: The influence of sulphurous compounds on metal pipes is harmful. It has been reported that the presence of sulphides particles raised the proportions causing rust from 22 to 90%. The effect of sulphides is almost due to liberation of hydrogen sulphides which accelerates the attack of acids on the pipe metal.

## Slide 29: Causes of Corrosion of Metal Pressure Pipes
Biological action: Soil contains various types of bacteria both aerobic and anaerobic. Certain anaerobic bacteria are capable of rendering the oxygen present in sulphates, nitrates and carbonates available for the free oxygen and thereby corrosion will proceed pace. The most important sulphate reducing bacteria (Vibrio desulphuricans) which can cause serious attack on buried pipes when three conditions are satisfied:
  absence of oxygen as in many clayey soil,
  presence of proper food (organic matter) and other environmental conditions needed for the growth of bacteria and
  presence of large amount of sulphates.

## Slide 30: Causes of Corrosion of Metal Pressure Pipes
Cavitation: The effects of cavitations are similar to those of corrosion but are due more to erosion. The sudden and alternate making and breaking of high vacuum and the creation and condensation of water vapour cause a bombardment of the surrounding surfaces with particles of water and water vapour moving at a high velocity thereby accelerating corrosion.
Temperature: The increase in temperature accelerates the rate of corrosion. The rate of corrosion in water pipes may be increased in three or four fold by raising the temperature from 60 to 1500 F.
Velocity of flowing water: As the velocity of the water in the pipe increases from linear to turbulence type, the rate of corrosion is sharply increased.

## Slide 31: Effect of Corrosion
Corrosion of water pipes causes a great economic loss. Both direct and indirect losses resulting from corrosion are vast and undesirable.
Replacing a corroded leaky water main by the roadside is very difficult and costly.
Corrosion greatly reduces the pressure head and results in increases cost of pumping and short life of the water mains.
Leakage in domestic plumbing fixtures due to corrosion involves not only the replacement but also repairing damages to walls, floors, etc.
Rusty water due to corrosion causes strain in cloth after washing, produces unsightly marks on the plumbing fixtures and unsuitable for domestic uses.

## Slide 32: Control of Corrosion
Corrosion of metal pipes may be reduced or eliminated by protection coatings of paint, galvanizing, bituminous compounds, or cement linings.
Red lead paint or zinc pigments offer some protection and are used on the exterior or exposed metal pipes.
Other metallic protective coatings are tin coatings, nickel coatings, chromium coatings and copper coatings.
Galvanizing by dipping the pipe molten zinc is an effective corrosion control except for highly acid waters. Galvanized pipe is widely used for small service lines in distribution systems but is too expensive for large pipe.
Large pipes are usually protected by non-metallic coatings, such as bituminous coatings or cement linings. Numerous commercial bituminous compounds are available for both hot and cold application.

## Slide 33: Scale Formation in Pressure Pipes
Scale formation in water pipes is mainly due to the presence of dissolved mineral matter and gases under favorable conditions of temperature and pressure.
Scale formation caused water pipes to wear out and burst out very soon as the cross-sections of the pipes are reduced and this also causes insufficient discharge through pipes.
Scaling also causes water unfit for domestic and industrial uses.

## Slide 34: Scale Formation in Pressure Pipes
The impurities which are mainly responsible for scale formation in water pipes may be classified under two heads: (i) Dissolved mineral matter and (ii) Dissolved gases.
Dissolved mineral matter include the hardness producing substances, i.e., carbonates, bicarbonates, sulphates and chlorides of calcium and magnesium, and silica.
Dissolved gases include carbon dioxide, oxygen, nitrogen, hydrogen sulphide and methane.

## Slide 35: Control of Scale Formation
To control scale formation in pressure pipes, water is softened.
The chief objective of water softening is to remove dissolved mineral compounds which constitute the hardness and which deposit scales in water pipes, boilers and hot water heating system cause serious difficulties in many processes including textile finishing, dying, canning, paper making, cold drinks preparation, tanning and others.
Following are the effective processes by which scale forming minerals and gases are removed from water: (i) Lime-soda process, (ii) Zeolite process, (iii) Phosphate process and (iv) Lime process.

## Slide 36: Environmental Engineering-1
CE3141
Lecture -3
Week-3, Saturday
02-04-2022

## Slide 37: Forces Acting on Pipes
Pipes carrying water under pressure must be designed to withstand stresses caused by internal and external loads, and temperature changes, and to satisfy the structural and hydraulic requirements.
The forces acting on pipes are:
Internal forces due to static head
Internal forces due to water hammer
Forces at bends and changes in cross-section
Forces due to temperature changes
External forces in the form of backfill, traffic and own weights.

## Slide 38: Internal Forces due to Static Head
Internal forces due to static head create hoof stress (transverse stress or circumferential stress) and longitudinal stress.
Hoof stress, Sh = pd/2t
Where, Sh = hoof stress per linear length in inch of the pipe.
P = intensity of static pressure in psi = wh, in which h is the static head and w is the unit weight of water.
d = pipe diameter in inch.
t = thickness of the pipe shell in inch.
Longitudinal (tensile) stress, St = pd2/[4t(d+t)] = pd/4t (approximately)

## Slide 39: Internal Forces due to Water Hammer
One of the most damaging factors to a water piping system is water hammer action. In addition to its effect on the piping system, water hammer causes banging noises in the system that is very disagreeable to occupants in the building. Water hammer occurs when a column of water flowing through a pipe line and discharging at an open outlet, is suddenly stopped by closing the outlet. Since flowing water has force, tremendous pressure result at the point of closure and pressure surges move along the pipe.

## Slide 40: Internal Forces due to Water Hammer
Phase 1: The valve on the line is closed and the water contained in the line is at rest. Water pressure is thus exerted in all directions in an equal way.
Phase 2: The valve on the line is open and water flow freely through the open outlet. Now the water pressure is utilized to force the water out of the open end of the pipe. Arrows indicate the direction of force in the column of water.
Valve
Valve

## Slide 41: Internal Forces due to Water Hammer
Phase 3: When the valve is quickly closed, the column of freely flowing water is suddenly stopped; excessively high pressures are generated at the point of stoppage. This creation is the same as would result of a steel bar moving through the line at the velocity of water were suddenly stopped by the valve.
Valve

## Slide 42: Internal Forces due to Water Hammer
Phase 4: In an effort to equalize the pressure build-up of the water, a shock wave will travel back along the branch line until a large diameter pipe is reached. This will allow the shock wave to dissipate itself. Arrows denote the direction of force towards the valve and then its reversal as a shock wave towards the point of relief. Since the shock wave travels at speeds in excess of 4000 fps, it causes a piping clatter all along its route. Often the shock wave will oscillate back and forth between the valve and the point of relief until the pressure is stabilized with the branch line.
Valve

## Slide 43: Internal Forces due to Water Hammer
The pressure generated by the shock wave can expand and often rupture the piping. Although piping clatter is normally associated with water hammer, you cannot assume that when these noises do not occur, that the shock wave is non-existent. Quite often, water hammer takes place without any physical sounds. Therefore, it is very important that piping system be designed with all due consideration given to the means that compensate for the action of water hammer.

## Slide 44: Methods of controlling water hammer
The maximum pressure developed in pipe line due to water hammer is given by the formula
P = 14.762V/√(1+Kd/t)
Where, V =Velocity of water just before the closing of the valve
d = Diameter of pipe
t = Thickness of pipe shell
K = Constant = Modulus of elasticity of pipe material/ Bulk modulus of elasticity of water

## Slide 45: Methods of controlling water hammer
In order to eliminate the damage and piping clatter that results from water hammer, it is important that certain steps be taken in piping system design to compensate for the excessive pressures that are generated when a column of flowing water is suddenly stopped.
The consideration is needed in some means or device that will provide flexibility in the system to absorb the initial shock wave of water hammer thereby conflicting the action to a given section of piping.
Air is the most effective medium for absorbing the shock wave caused by water hammer for (i) water is non-compressible; (ii) air can be compressed to considerable pressure when the water compresses the air, it also fills the void offered by the displaced air. Because water has this flexible means to expend its force, the shock wave that would otherwise result, is quickly absorbed.

## Slide 46: Methods of controlling water hammer
Valve
Entrapped air
Air chamber
Water Branch line
Flow
Entrapped air
Air chamber
Water Branch line
Flow
Water at rest
Discharging freely

## Slide 47: Forces at Bends and Changes in Cross-section
A change in direction magnitude of flow velocity is accompanied by a change in the momentum of water. The force required to produce this change in momentum covers from pressure variation within the water and from the forces transmitted to the water from the pipe walls. For a pipe bend of the uniform section,
Longitudinal force = s(d)t
Where, s is the unit stress, d is the diameter of the pipe and t the wall thickness of the pipe.
Similar expression for forces developed for a pipe bend of non-uniform cross-section, pipe contraction and enlargement can be computed. These stresses can be eliminated or reduced by providing an efficient anchorage at the bend, contraction and enlargement.

## Slide 48: Forces due to Temperature Changes
Longitudinal stress of considerable magnitude may develop in pipes exposed to large changes in temperature. The change in length  of a pipe length L when subjected to a temperature change T is,
 = L.T
where  is the coefficient of thermal expansion of the pipe material. If this change in length is prevented, longitudinal stress will develop. The amount of these stresses may be calculated by the formula:
f = ET
where, E is the thermal modulus of elasticity of pipe material
This indicates the longitudinal stress that would result when a pipe with fixed ends is subjected to a temperature change. Expansion joints are usually provided to reduce temperature stresses.

## Slide 49: External Forces
Pipes are often placed in an excavated trench which is back filled, or they are laid on ground surface and covered with earth. In either case a vertical load is imposed on the pipe. If a load is superimposed on the fill, a portion of it will be transferred to the buried pipe. The magnitude of the load thus produced depends on the rigidity of the pipe, the type of bedding and the character of the fill material.
1. According to Anson Marston, for rigid pipes in narrow trenches, the load w in pound per foot of pipe has been found to be,
w = cB2
where B is the trench width at the top of the pipe,  is the specific weight of the fill material, and c is the coefficient characteristics of the fill material, and the ratio of cover depth to the width of the trench, and is generally termed as load calculation coefficient.

## Slide 50: External Forces
If the pipe is flexible type, and the soil at the sides is well compacted, the side fills may be expected to carry their proportional share of the total load. The empirical formula for the load on the buried flexible pipe in a narrow trench is,
w = cBD
where D is the out side diameter of the pipe.
If the pipe is placed on undisturbed ground and covered with fill (as highway culvert), the equation for the load on buried pipe under embankment conditions is,
w =cp D2
value of cp depends on the type of the pipe and characteristics of the foundation and backfill.

## Slide 51: External Forces
The formula for load due to super imposed concentrated load is given in the following form by D.H.Holl’s integration of Bousainesq’s formula as,
wsc = (c1psc) I/L
where wsd is superimposed concentrated load on pipe in lb/ft, psc is the superimposed concentrated load in lb, I is the impact factor and c1 is the load coefficient which is a function of D/2H and L/2H. In case distributed superimposed load, the expression for load on the pipe is,
wsd = c1pID
where wsd is the superimposed distributed load on the pipe in lb/ft length, p is the intensity of distributed load in lb/sq.ft, c1 is the load coefficient which is function of N/2H and M/2H.

## Slide 52: External Forces

## Slide 53: WATER DISTRIBUTION SYSTEM
The distribution system is that part of the water-work which receives the water from the pumping station or from treatment plant and delivers it throughout the district to be served.
It includes, such as, reservoirs for purposes of storage, equalizing pressures and subsequent distribution, together with pipes, valves, hydrants and other appurtenance for carrying water, service pipe and meters etc.

## Slide 54: Objectives of Distribution System
The main purposes of the construction of water distribution system are:
To make water available in close proximity to the consumer;
To supply water in adequate quantities according to the demand of the consumers;
To supply water with adequate pressure;
To regulate water supply as per requirement.

## Slide 55: General consideration for water distribution system
The general considerations of the planning of distribution system should be observed in its design:
Circulation of water: The layout of distribution system should be such that there is free circulation of water and that the number of dead ends should be very few. Where dead ends are unavoidable, the hydrants will be provided to act as washouts.
Construction and design: The construction and design of water distribution system should be such that ample water is available at all times at desired pressure in all portion of the distribution system.

## Slide 56: General consideration for water distribution system
The minimum residual pressures at ferrule point for direct supply to single-storeyed, two-storeyed and three-storeyed buildings should be respectively 7 m, 12 m and 17 m. If the available pressure in the pipe is low, it has to be boosted up with the help of fire engines in case of fire occurrence. In general, the construction and design of the water distribution system be such that it can be relied upon even for meeting future expansion programs.
Earth cushioning: The mains, which are laid under roads, should be provided with a minimum earth cushioning of 900 mm height from the top of mains. At other places, the cushioning may be of 750 mm height.

## Slide 57: General consideration for water distribution system
Construction by sewage: The water pipe line should be laid above the sewers at a vertical distance of about 2 m and the horizontal distance between the water pipes and sewer should be at least 3 m. If the physical configuration of country does not permit the provision of this minimum spacing, extraordinary precautions should be taken to make the distribution system watertight to the maximum possible extent.
Fire demand: The distribution system should be so laid that the water for fire demand is available in required quantity at desired pressure at number of points along it.

## Slide 58: General consideration for water distribution system
Economy: The layout and design of distribution system should be economical. The cost of distribution system forms a substantial part to extent of about 90% of the total cost of the water supply project. Hence the water distribution system should be carefully designed by taking into various factors such as pumping head, type of pipes, storage requirement, pipe diameter, etc.
Gradients: It is not necessary to lay mains at constant gradients. But the gradients of mains should in general follow the natural contour of ground. The gradient line should not rise above the hydraulic gradient line which means that at every points along the mains, there should be a positive pressure gradient than the atmospheric pressure.

## Slide 59: General consideration for water distribution system
Leakage: The distribution system should be fairly watertight and the loss of water due to leakage should be brought down to the minimum possible extent.
Repairs: The distribution system should be so laid as to permit easy repairs. The broken or worn out parts of the equipments for various operations should be properly replaced.
Safety from pollution: The layout of distribution system should be such that it does not contribute to the pollution of water flowing in it.
Sanitation: The sanitation of area through which the distribution system is passing should be good so that there are no chances for water to be polluted during repairs or replacements of pipe lines.
Unsafe cross connection: The distribution system should not have any unsafe cross connection from which there are chances for contaminated water to enter it.